## Municipal
Town of Sudbury: Priority for ADA Transition Plan - Municipal Buildings | Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Column11 | Column12 | Column13 | Column14
| Priorities: Priority 1: Program Access* or Safety Priority 2: Navigational Issue Priority 3: Additional Access* Priority 4: Enhanced Usability | *Note: Some toilet rooms issues compromise Program Access. Some toilet rooms with less central issues (e.g., partially accessible toilet rooms), fall under Additional Access. | **IHCD Cost Estimation Notes: - Cost of design is not included. - Does not include costs when note indicates future work. - Labor cannot be estimated for all remedies. - There is no cost noted when it's presumed to be a maintenance issue. - Cost based on a national average. Cost is not based on prevailing wage. - There is no cost noted when it's presumed to be a maintenance issue. Estimates are intended as a guide to budgeting access modifications and are not intended to be absolutely comprehensive or definitive.
| Information Provided by Institute for Human Centered Design | [10 empty] | Project Management for the Town of Sudbury
ID | Facility Name | Element | Issue/Physical Barrier | Location | Floor | Room | Town Priority | Priority for Barrier Removal | Remedies | Quantity | Estimated Cost of Barrier Removal | Project Start Date | Project Completion Date | Responsible for Barrier Removal
1 | DPW Offices and Garage | A. Exterior Access Route | B. Exterior route < 36" wide C. Exterior route < 48" wide | Front Walkway | Exterior | N/A | Priority 1 | Program Access | Ensure that a clear width of 36" min. is maintained at the accessible route with 48" preferred per 521 CMR. Relocate car charging station so that there is 36" clear min. Trim hedges and install wheel stops so that vehicles do not block the sidewalk. (Cost is beyond the scope of the project.) | 1 | 0
2 | DPW Offices and Garage | C. Off-Street Parking Lot or Garage | L. Access aisle does not adjoin an accessible route | Parking Lot - Car Accessible Space Access Aisle | Exterior | N/A | Priority 1 | Program Access | Ensure the access aisle by the car accessible space adjoins an accessible route. Provide a curb ramp. | 1 | 2800
3 | DPW Offices and Garage | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) L. Mat not securely attached | Central Exit | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. Secure the mat. | 1 | 432
4 | DPW Offices and Garage+Table1[#All]+Table1[#All] | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) L. Mat not securely attached | South Exit | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. Secure the mat. | 1 | 432
5 | DPW Offices and Garage | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) L. Mat not securely attached | North Exit | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. Secure the mat. | 1 | 432
6 | DPW Offices and Garage | B. Interior Access Route | A. Route < 36" wide | Women’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate table to ensure that a clear width of 36" min. is maintained at the accessible route. Route is allowed to narrow to narrow to 32" for a depth of 24". | 1 | 0
7 | DPW Offices and Garage | B. Interior Access Route | A. Route < 36" wide | Board of Health | 1 | N/A | Priority 3 | Additional Access | Relocate cabinets to ensure that a clear width of 36" min. is maintained at the accessible route. | 1 | 0
8 | DPW Offices and Garage | B. Interior Access Route | B. Obstructed by protruding objects | Corridor by Main Entrance | 1 | N/A | Priority 3 | Additional Access | Relocate or recess fire alarm box. | 1 | 256
9 | DPW Offices and Garage | B. Interior Access Route | B. Obstructed by protruding objects | Application Forms Area/ Overlook | 1 | N/A | Priority 3 | Additional Access | Provide a cane-detectable barrier on the open side of the high counter. | 1 | 306
10 | DPW Offices and Garage | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Near Main Entrance | 1 | N/A | Priority 3 | Additional Access | Secure mats. | 2 | 0
11 | DPW Offices and Garage | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Transfer Station Cemetery Department | 1 | N/A | Priority 3 | Additional Access | Secure mat. | 1 | 0
12 | DPW Offices and Garage | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Women’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate trash container so that there is 18" min. on the pull side of the door. | 1 | 0
13 | DPW Offices and Garage | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Conference Room | 1 | N/A | Priority 3 | Additional Access | Relocate table so that there is 18" min. on the latch side of the door. | 1 | 0
14 | DPW Offices and Garage | H. Signage | G. Sign not located on the latch side of the door | Transfer Station Cemetery Department | 1 | N/A | Priority 2 | Navigational Issue | Locate sign at permanent rooms alongside the door on the latch side. | 1 | 0
15 | DPW Offices and Garage | H. Signage | Z. Signage lacks clear floor space | Engineering Near Main Entrance | 1 | N/A | Priority 2 | Navigational Issue | Remove the plastic container to ensure that a clear floor space of 18" by 18" is centered on the tactile characters. | 1 | 0
16 | DPW Offices and Garage | H. Signage | Z. Signage lacks clear floor space | Conservation | 1 | N/A | Priority 2 | Navigational Issue | Remove the file folder to ensure that a clear floor space of 18" by 18" is centered on the tactile characters. | 1 | 0
17 | DPW Offices and Garage | K. Operable Parts | C. Reach < 15" or > 48"(forward/side approach) | Application Forms Area/ Overlook | 1 | N/A | Priority 3 | Additional Access | Relocate one of each form to be located between 15"- 48" above the finished floor. | 1 | 0
18 | DPW Offices and Garage | K. Operable Parts | C. Reach < 15" or > 48"(forward/side approach) | Transfer Station Cemetery Department | 1 | N/A | Priority 3 | Additional Access | Relocate clothes rod to be no higher than 48" above the finished floor. | 1 | 256
19 | DPW Offices and Garage | K. Operable Parts | C. Reach < 15" or > 48"(forward/side approach) | Transfer Station Cemetery Department | 1 | N/A | Priority 3 | Additional Access | Relocate one of each form to be located between 15"- 48" above the finished floor. | 1 | 0
20 | DPW Offices and Garage | K. Operable Parts | C. Reach < 15" or > 48"(forward/side approach) | Corridor Near Mail/Copy Room | 1 | N/A | Priority 3 | Additional Access | Relocate one of each form to be located between 15"- 48" above the finished floor. | 1 | 0
21 | DPW Offices and Garage | K. Operable Parts | C. Reach < 15" or > 48"(forward/side approach) | Corridor Near Mail/Copy Room | 1 | N/A | Priority 3 | Additional Access | Relocate one of each form to be located between 15"- 48" above the finished floor. | 1 | 0
22 | DPW Offices and Garage | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Conservation | 1 | N/A | Priority 1 | Program Access | Provide at least 1 dining or work surface with 27" min. knee and toe clearance. | 1 | 700
23 | DPW Offices and Garage | M. Dining or Work Surfaces | Z. Clear floor space not provided at work surface | Director of Operations | 1 | N/A | Priority 3 | Additional Access | Relocate desk so that there is 48" clear min. | 1 | 0
24 | DPW Offices and Garage | M. Dining or Work Surfaces | Z. Clear floor space not provided at work surface | Conservation | 1 | N/A | Priority 3 | Additional Access | Relocate desk so that there is 48" clear min. | 1 | 0
25 | DPW Offices and Garage | S. Picnic Tables | H. Picnic table not on an accessible route | Picnic Table by North Exit | Exterior | N/A | Priority 1 | Program Access | Ensure that the dining surface is connected to an accessible route. (Cost estimate for a 6' long 4' wide concrete route.) | 1 | 384
26 | DPW Offices and Garage | B. Lavatory | G. Dispensers not within reach range | Men's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Lower the soap dispenser to 42" max. above the floor. | 1 | 353
27 | DPW Offices and Garage | D. Toilet Compartment | C. Door has non-compliant hardware | Women’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 70
28 | DPW Offices and Garage | D. Toilet Compartment | C. Door has non-compliant hardware D. Door has malfunctioning self-closing hinge | Men's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. Repair hinge. | 1 | 70
29 | DPW Offices and Garage | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Women’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
30 | DPW Offices and Garage | D. Toilet Compartment | N. Non-compliant toilet paper dispenser | Women’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Remove toilet paper dispenser that is mounted above the grab bar. | 1 | 353
31 | DPW Offices and Garage | E. Urinal | D. Urinal recessed > 24" has > 36" clear width | Men's Toilet Room | 1 | N/A | Priority 3 | Additional Access | If urinal is recessed greater than 24" ensure there is a clear width of 36". Relocate the partition. | 1 | 353
32 | DPW Offices and Garage | F. Dispensers | C. Not operable with a closed fist | Women’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Provide a dispenser that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 1000
33 | DPW Offices and Garage | F. Dispensers | D. Dispenser acts as a protruding object | Women’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate paper towel dispensers out of the circulation path. | 2 | 512
34 | DPW Offices and Garage | F. Dispensers | D. Dispenser acts as a protruding object | Men's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate paper towel dispensers out of the circulation path. | 2 | 512
35 | DPW Offices and Garage | A. Drinking Fountains | H. No drinking fountain provided for standing users L. Knee or toe clearance not provided | Drinking Fountain Near Women’s Toilet Room | 1 | N/A | Priority 1 | Program Access | Install a Hi-Lo drinking fountain. Provide knee and toe clearance, 27" min. high at drinking fountain for seated users. | 1 | 4216
36 | DPW Offices and Garage | N/A | N/A | DPW Garage | 1 | N/A | Priority 4 | Enhanced Usability | Garage is not currently accessed by members of the public. | 1 | 0
37 | DPW Offices and Garage | N/A | N/A | Main Entrance | 1 | N/A | Priority 4 | Enhanced Usability | This is a good example of a recessed floor mat. | 1 | 0
38 | DPW Offices and Garage | N/A | N/A | Engineering Near Main Entrance | 1 | N/A | Priority 4 | Enhanced Usability | Recommend increasing lighting in this area so that signage is more legible. | 1 | 0
39 | DPW Offices and Garage | N/A | N/A | Engineering Conference Room | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing designation sign with raised character and braille even though a sign is not provided. | 1 | 0
40 | DPW Offices and Garage | N/A | N/A | Front Walkway | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing an accessible vehicle charging station with 3' min. access aisles on each side and a 10'-13' wide vehicle space. | 1 | 0
41 | DPW Offices and Garage | N/A | N/A | Picnic Table by North Exit | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing an accessible 48-inch wide route around the picnic table with concrete, asphalt or stone dust. | 1 | 0
1 | Fairbank Community Center | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) L. Does not prevent accumulation of water | Kids Summer Camp Entrance | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%) and ensure that running slope is no greater than 1:50 (2.00%) at the gate. Repair surface so that it does not accumulate water. (Cost estimate for a 10' long by 4' wide asphalt route.) | 1 | 400
2 | Fairbank Community Center | A. Exterior Access Route | K. Surface is not stable, firm, and slip-resistant | Basketball Court Northeast Walkway | Exterior | N/A | Priority 3 | Additional Access | Patch and repair asphalt surface. | 1 | 160
3 | Fairbank Community Center | C. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces C. Total # of designated van accessible spaces F. Running or cross slope at space > 1:50 (2.00%) | West Parking Lot | Exterior | N/A | Priority 1 | Program Access | Reduce running or cross slope at north accessible parking space to be no steeper than 1:50 (2.00%). | 1 | 1440
4 | Fairbank Community Center | C. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces C. Total # of designated van accessible spaces F. Running or cross slope at space > 1:50 (2.00%) O. Sign does not have the designation "Van Accessible" P. Sign bottom < 60" above finished grade | Parking Lot on Northeast Side | Exterior | N/A | Priority 1 | Program Access | Provide one van accessible space. Add the designation "Van Accessible" to the sign at the larger van accessible parking space. Reduce running or cross slope to be no steeper than 1:50 (2.00%). Locate signs with the bottom of the sign 60" min. above the ground. | 1 | 1940
5 | Fairbank Community Center | E. Exterior Ramp | C. Running slope > 1:12 (8.3%) F. Handrails not provided at both sides if rise is > 6" R. Surface is not stable, firm, and slip-resistant | Route Between Pool and Picnic Table Area | 1 | N/A | Priority 3 | Additional Access | Install a temporary metal ramp to provide an accessible route. (Cost is for a 7' perforated metal ramp with a 5' x 5' platform courtesy of Amramp.) | 1 | 2800
6 | Fairbank Community Center | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided | Pool Egress With Step by the Gate | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. | 1 | 464
7 | Fairbank Community Center | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided | Pool Egress to Stepping Stone Path | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. | 1 | 464
8 | Fairbank Community Center | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided | Egress by Pool Locker Rooms to Senior Center Parking Lot | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. | 1 | 464
9 | Fairbank Community Center | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided | Egress Through Sudbury Pines Room | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. | 1 | 464
10 | Fairbank Community Center | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Diving Pool Egress to Picnic Table Area | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
11 | Fairbank Community Center | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Egress Next to Gym/Stage | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
12 | Fairbank Community Center | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Gym/Stage Egress | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
13 | Fairbank Community Center | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Main Entrance to Pool | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
14 | Fairbank Community Center | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Egress Next to Toilet Rooms in the Senior Center | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 1116
15 | Fairbank Community Center | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Senior Center Main Exit and School Department Main Exit | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 2 | 864
16 | Fairbank Community Center | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) G. Maneuvering clearance(s) not provided | Egress Through Kitchen | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. Relocate refrigerator to provide 12 inches clear on the latch side of the door, | 1 | 1116
17 | Fairbank Community Center | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Route to Gym/Stage | 1 | N/A | Priority 3 | Additional Access | Secure mats. | 1 | 0
18 | Fairbank Community Center | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Director of Student Services | 1 | N/A | Priority 3 | Additional Access | Secure carpet. | 1 | 0
19 | Fairbank Community Center | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Human Resources | 1 | N/A | Priority 3 | Additional Access | Secure carpet. | 1 | 0
20 | Fairbank Community Center | B. Interior Access Route | H. Accessible route not provided | Pre-school Multipurpose Room | 1 | N/A | Priority 1 | Program Access | Provide a portable ramp at 2" level change. | 1 | 500
21 | Fairbank Community Center | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Secondary Entrance to Pool | 1 | N/A | Priority 3 | Additional Access | Provide an automatic door opener. | 1 | 3060
22 | Fairbank Community Center | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Director’s and First Aid Office by Pool | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
23 | Fairbank Community Center | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Teen Room | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
24 | Fairbank Community Center | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Business Office | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
25 | Fairbank Community Center | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Senior Center Volunteer Program Coordinator | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
26 | Fairbank Community Center | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Room 3 Game Room by Parks and Recreation | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
27 | Fairbank Community Center | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Pre-school Room by Parks and Recreation | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
28 | Fairbank Community Center | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Social Worker for District | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
29 | Fairbank Community Center | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Assistant Director of Student Services | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
30 | Fairbank Community Center | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Human Resources | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
31 | Fairbank Community Center | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist M. Door requires > 5 lbs. of force to open | Pool Entrance | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. Adjust closers so doors do not require more than 5 pounds of force to open. | 1 | 484
32 | Fairbank Community Center | C. Doors, Doorways, & Gates | M. Door requires > 5 lbs. of force to open | Secondary Entrance to Pool | 1 | N/A | Priority 3 | Additional Access | Adjust closers so doors do not require more than 5 pounds of force to open. | 1 | 0
33 | Fairbank Community Center | C. Doors, Doorways, & Gates | M. Door requires > 5 lbs. of force to open | All Gender Toilet Room by Locker Rooms (West Side) | 1 | N/A | Priority 3 | Additional Access | Adjust closers so doors do not require more than 5 pounds of force to open. | 1 | 0
34 | Fairbank Community Center | C. Doors, Doorways, & Gates | M. Door requires > 5 lbs. of force to open | All Gender Toilet Room by Locker Rooms (East Side) | 1 | N/A | Priority 3 | Additional Access | Adjust closers so doors do not require more than 5 pounds of force to open. | 1 | 0
35 | Fairbank Community Center | C. Doors, Doorways, & Gates | M. Door requires > 5 lbs. of force to open | Women's/ Girls' Toilet Room by Human Resources | 1 | 30 | Priority 3 | Additional Access | Adjust closers so doors do not require more than 5 pounds of force to open. | 1 | 0
36 | Fairbank Community Center | C. Doors, Doorways, & Gates | M. Door requires > 5 lbs. of force to open | Men’s/Boys' Toilet Room by Human Resources | 1 | N/A | Priority 3 | Additional Access | Adjust closers so doors do not require more than 5 pounds of force to open. | 1 | 0
37 | Fairbank Community Center | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Pool - Men's Locker Room | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
38 | Fairbank Community Center | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Pool - Women’s Locker Room Access From the Reception | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
39 | Fairbank Community Center | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Women’s Locker Room Entrance From Pool Side | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
40 | Fairbank Community Center | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Senior Center Secondary Entrance Next to Gym/Stage | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
41 | Fairbank Community Center | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Assistant Superintendent and Superintendent | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 2 | 464
42 | Fairbank Community Center | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Student Services | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
43 | Fairbank Community Center | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Social Worker for District | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
44 | Fairbank Community Center | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Business Office Clerk and Accounting | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
45 | Fairbank Community Center | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Business Office | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
46 | Fairbank Community Center | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Human Resources | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
47 | Fairbank Community Center | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Room 3 Game Room by Parks and Recreation | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
48 | Fairbank Community Center | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign G. Sign not located on the latch side of the door | Senior Center Volunteer Program Coordinator | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. Locate sign at permanent rooms alongside the door on the latch side. | 1 | 232
49 | Fairbank Community Center | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign G. Sign not located on the latch side of the door | Women's/ Girls' Toilet Room by Human Resources | 1 | 30 | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. Locate sign at permanent rooms alongside the door on the latch side. | 1 | 232
50 | Fairbank Community Center | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign G. Sign not located on the latch side of the door | Men’s/Boys' Toilet Room by Human Resources | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. Locate sign at permanent rooms alongside the door on the latch side. | 1 | 232
51 | Fairbank Community Center | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign G. Sign not located on the latch side of the door | Senior Center, M. Van Houten Room | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. Locate sign at permanent rooms alongside the door on the latch side. | 1 | 232
52 | Fairbank Community Center | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign G. Sign not located on the latch side of the door | Senior Center, Sudbury Pines Room | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. Locate sign at permanent rooms alongside the door on the latch side. | 1 | 232
53 | Fairbank Community Center | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign G. Sign not located on the latch side of the door | Senior Center, Administrative Coordinator | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. Locate sign at permanent rooms alongside the door on the latch side | 1 | 232
54 | Fairbank Community Center | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign G. Sign not located on the latch side of the door | Senior Center, Program Coordinator | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. Locate sign at permanent rooms alongside the door on the latch side. | 1 | 232
55 | Fairbank Community Center | H. Signage | G. Sign not located on the latch side of the door | All Gender Toilet Room by Locker Rooms (West Side) | 1 | N/A | Priority 2 | Navigational Issue | Locate sign at permanent rooms alongside the door on the latch side. | 1 | 0
56 | Fairbank Community Center | H. Signage | G. Sign not located on the latch side of the door | All Gender Toilet Room by Locker Rooms (East Side) | 1 | N/A | Priority 2 | Navigational Issue | Locate sign at permanent rooms alongside the door on the latch side. | 1 | 0
57 | Fairbank Community Center | H. Signage | G. Sign not located on the latch side of the door | Senior Center, Women's and Men's Toilet Rooms | 1 | N/A | Priority 2 | Navigational Issue | Locate sign at permanent rooms alongside the door on the latch side. | 2 | 0
58 | Fairbank Community Center | J. Service Counter | B. Counter > 36" high | Senior Center Main Reception | 1 | N/A | Priority 3 | Additional Access | Provide a counter that is 36" max. above the ground or finished floor. | 1 | 880
59 | Fairbank Community Center | J. Service Counter | B. Counter > 36" high | Concession Stand at Kids Summer Camp (Interior of Fence) | Exterior | N/A | Priority 3 | Additional Access | Provide a counter that is 36" max. above the ground or finished floor. | 1 | 880
60 | Fairbank Community Center | J. Service Counter | B. Counter > 36" high | Concession Stand (Exterior of Fence) | Exterior | N/A | Priority 3 | Additional Access | Provide a counter that is 36" max. above the ground or finished floor. | 1 | 880
61 | Fairbank Community Center | K. Operable Parts | C. Reach < 15" or > 48"(forward/side approach) | Pool - Main Entrance | 1 | N/A | Priority 3 | Additional Access | Ensure that one of each type of form is located no higher than 48" above the finished floor. | 1 | 0
62 | Fairbank Community Center | K. Operable Parts | D. Side reach > 54" | Diving Pool Coat Hooks | 1 | N/A | Priority 3 | Additional Access | Provide one hook at 48" max. above the finished floor. | 1 | 150
63 | Fairbank Community Center | K. Operable Parts | D. Side reach > 54" | Swimming Pool Coat Hooks | 1 | N/A | Priority 3 | Additional Access | Provide one hook at 48" max. above the finished floor. | 1 | 150
64 | Fairbank Community Center | L. Children's Reach Ranges | C. Reach < 20" or > 36" (Ages 3 - 4) | Pre-school Multipurpose Room | 1 | N/A | Priority 3 | Additional Access | Provide one storage hook and shelf that is between 20" and 36" above the finished floor. | 1 | 0
65 | Fairbank Community Center | N. Assembly Area | N. Accessible route to stage not provided | Gym/Stage | 1 | N/A | Priority 1 | Program Access | Provide an interior lift to the stage. | 1 | 21660
66 | Fairbank Community Center | O. Locker Room | M. Room is < 78" x 72" Q. Bench < 24" deep R. Bench < 48" long | Pool - Women’s Locker Room Changing Rooms | 1 | N/A | Priority 1 | Program Access | Provide an accessible changing room that is 78" by 72" minimum. Provide a bench that is 24" deep and 48" long with room on the side to transfer. | 1 | 5866
67 | Fairbank Community Center | O. Locker Room | O. Back support not provided at bench P. Bench is not 17"-19" high Q. Bench < 24" deep R. Bench < 48" long | Pool - Women’s Locker Room | 1 | N/A | Priority 3 | Additional Access | Provide at least one bench with back support or that is affixed to a wall with room on the side to transfer. Install a bench with the top of the seat between 17"- 19" above the finished floor. Provide a bench that is 24" deep and 48" long. | 1 | 200
68 | Fairbank Community Center | O. Locker Room | O. Back support not provided at bench Q. Bench < 24" deep R. Bench < 48" long | Pool - Men's Locker Room | 1 | N/A | Priority 3 | Additional Access | Provide at least one bench with back support or that is affixed to a wall with room on the side to transfer. Provide a bench that is 24" deep and 48" long. | 1 | 200
69 | Fairbank Community Center | O. Locker Room | T. Hook > 48" high | Pool - Men's Locker Room | 1 | N/A | Priority 3 | Additional Access | Locate one hook no higher than 48" above the finished floor. | 1 | 150
70 | Fairbank Community Center | O. Locker Room | T. Hook > 48" high | Pool - Men's Showers and Women's Showers | 1 | N/A | Priority 3 | Additional Access | Locate one hook no higher than 48" above the finished floor. | 2 | 300
71 | Fairbank Community Center | O. Locker Room | T. Hook > 48" high | Pool - Women’s Locker Room | 1 | N/A | Priority 3 | Additional Access | Locate one hook no higher than 48" above the finished floor. | 1 | 150
72 | Fairbank Community Center | O. Locker Room | T. Hook > 48" high | Pool - Women’s Locker Room Changing Rooms | 1 | N/A | Priority 3 | Additional Access | Locate one hook no higher than 48" above the finished floor. | 1 | 150
73 | Fairbank Community Center | O. Locker Room | T. Hook > 48" high | Pool - Women’s Locker Room | 1 | N/A | Priority 3 | Additional Access | Locate one hook no higher than 48" above the finished floor. | 1 | 150
74 | Fairbank Community Center | S. Picnic Tables | G. Toe or knee clearance at tables not provided H. Picnic table not on an accessible route | Picnic Table Next to Northeast Parking Lot Accessible Parking by Street | Exterior | N/A | Priority 1 | Program Access | Provide at least 1 picnic table in this area with toe and knee clearance. Ensure that the picnic table is connected to an accessible route. | 1 | 1400
75 | Fairbank Community Center | S. Picnic Tables | H. Picnic table not on an accessible route | Picnic Area | Exterior | N/A | Priority 1 | Program Access | Ensure that the accessible space at the picnic tables are connected to an accessible route. | 2 | 0
76 | Fairbank Community Center | U. Kitchens and Kitchenettes | A. Knee/toe clearance not provided at sink B. Sink > 34" high | Senior Center, M. Van Houten Room | 1 | N/A | Priority 1 | Program Access | Provide a sink with knee and toe clearance positioned for a forward approach. Ensure the sink is no higher than 34" above the finished floor. | 1 | 4780
77 | Fairbank Community Center | A. Overall Access | H. Audible and visible alarms not provided | Senior Center, Women's and Men's Toilet Rooms | 1 | N/A | Priority 3 | Additional Access | When fire system is updated, ensure that a visible and audible fire alarm is installed. | 2 | 0
78 | Fairbank Community Center | A. Overall Access | H. Audible and visible alarms not provided | All Gender Toilet Room(West Side) | 1 | N/A | Priority 3 | Additional Access | When fire system is updated, ensure that a visible and audible fire alarm is installed. | 1 | 0
79 | Fairbank Community Center | B. Lavatory | E. Plumbing underneath is exposed | Women's/ Girls' Toilet Room by Human Resources | 1 | 30 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at lavatory with knee and toe clearance. | 1 | 92
80 | Fairbank Community Center | B. Lavatory | E. Plumbing underneath is exposed | All Gender Toilet Room by Locker Rooms (East Side) | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at lavatory. | 1 | 92
81 | Fairbank Community Center | B. Lavatory | E. Plumbing underneath is exposed | Pool - Men's Locker Room | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact for at least one lavatory. | 1 | 92
82 | Fairbank Community Center | B. Lavatory | F. Mirror above lavatory w/reflective surface > 40" G. Dispensers not within reach range | Pool - Men's Locker Room | 1 | N/A | Priority 3 | Additional Access | Lower mirror so that the bottom surface is at 40" max. above the finished floor. Lower soap and paper towel dispensers to 42" max. above the floor. | 1 | 768
83 | Fairbank Community Center | B. Lavatory | E. Plumbing underneath is exposed | Pool - Women’s Locker Room | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact for at least one lavatory. | 1 | 92
84 | Fairbank Community Center | B. Lavatory | F. Mirror above lavatory w/reflective surface > 40" G. Dispensers not within reach range | Pool - Women’s Locker Room | 1 | N/A | Priority 3 | Additional Access | Lower mirror so that the bottom surface is at 40" max. above the finished floor. Lower soap and paper towel dispensers to 42" max. above the floor. | 1 | 768
85 | Fairbank Community Center | B. Lavatory | E. Plumbing underneath is exposed | Senior Center, Men’s Toilet Room | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact for at least one lavatory. | 1 | 92
86 | Fairbank Community Center | B. Lavatory | F. Mirror above lavatory w/reflective surface > 40" G. Dispensers not within reach range | Senior Center, Men’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Lower mirror so that the bottom surface is at 40" max. above the finished floor. Lower soap and paper towel dispensers to 42" max. above the floor. | 1 | 768
87 | Fairbank Community Center | B. Lavatory | E. Plumbing underneath is exposed | All Gender Toilet Room by Locker Rooms (West Side) | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at lavatory. | 1 | 92
88 | Fairbank Community Center | B. Lavatory | G. Dispensers not within reach range | All Gender Toilet Room by Locker Rooms (West Side) | 1 | N/A | Priority 3 | Additional Access | Lower paper towel dispenser to 42" max. above the floor. | 1 | 256
89 | Fairbank Community Center | B. Lavatory | E. Plumbing underneath is exposed | Senior Center, Women's Toilet Room | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact for at least one lavatory. | 1 | 92
90 | Fairbank Community Center | B. Lavatory | G. Dispensers not within reach range | Senior Center, Women's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Lower soap and paper towel dispensers to 42" max. above the floor. | 1 | 512
91 | Fairbank Community Center | B. Lavatory | E. Plumbing underneath is exposed | Men’s/Boys' Toilet Room | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at lavatory with knee and toe clearance. | 1 | 92
92 | Fairbank Community Center | B. Lavatory | G. Dispensers not within reach range | Men’s/Boys' Toilet Room | 1 | N/A | Priority 3 | Additional Access | Lower soap dispenser to 42" max. above the floor. | 1 | 353
93 | Fairbank Community Center | D. Toilet Compartment | C. Door has non-compliant hardware D. Door has malfunctioning self-closing hinge | All Gender Toilet Room by Locker Rooms (West Side) | 1 | N/A | Priority 3 | Additional Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. Repair hinge. | 1 | 70
94 | Fairbank Community Center | D. Toilet Compartment | C. Door has non-compliant hardware D. Door has malfunctioning self-closing hinge | All Gender Toilet Room by Locker Rooms (East Side) | 1 | N/A | Priority 3 | Additional Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. Repair hinge. | 1 | 70
95 | Fairbank Community Center | D. Toilet Compartment | C. Door has non-compliant hardware D. Door has malfunctioning self-closing hinge | Senior Center, Men’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. Repair hinge. | 1 | 70
96 | Fairbank Community Center | D. Toilet Compartment | C. Door has non-compliant hardware D. Door has malfunctioning self-closing hinge R. Coat hook > 48" | Pool - Men's Locker Room | 1 | N/A | Priority 3 | Additional Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. Repair hinge. Lower coat hook so that it is no higher than 48". | 1 | 220
97 | Fairbank Community Center | D. Toilet Compartment | C. Door has non-compliant hardware D. Door has malfunctioning self-closing hinge R. Coat hook > 48" | Senior Center, Women's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. Repair hinge. Lower coat hook so that it is no higher than 48". | 1 | 220
98 | Fairbank Community Center | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Pool - Women’s Locker Room | 1 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
99 | Fairbank Community Center | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Men’s/Boys' Toilet Room by Human Resources | 1 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
100 | Fairbank Community Center | D. Toilet Compartment | J. Side or rear grab bar < 33" or >36" high M. Flush control not on open side N. Non-compliant toilet paper dispenser | Senior Center, Men’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Locate side grab bar between 33"- 36" above the finished floor. Provide the flush control on the open side of the toilet (transfer side). Relocate toilet paper so that it is 24" min. high, located under the grab bar, and between 7" and 9" from the front of the toilet. | 1 | 1123
101 | Fairbank Community Center | D. Toilet Compartment | J. Side or rear grab bar < 33" or >36" high N. Non-compliant toilet paper dispenser | Senior Center, Women's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Locate side grab bar between 33"- 36" above the finished floor. Relocate toilet paper so that it is 24" min. high, located under the grab bar, and between 7" and 9" from the front of the toilet. | 1 | 749
102 | Fairbank Community Center | D. Toilet Compartment | M. Flush control not on open side | Pool - Women’s Locker Room | 1 | N/A | Priority 3 | Additional Access | Provide the flush control on the open side of the toilet (transfer side). | 1 | 374
103 | Fairbank Community Center | D. Toilet Compartment | M. Flush control not on open side N. Non-compliant toilet paper dispenser | All Gender Toilet Room by Locker Rooms (East Side) | 1 | N/A | Priority 3 | Additional Access | Provide the flush control on the open side of the toilet (transfer side). Relocate toilet paper so that it is 24" min. high, located under the grab bar, and between 7" and 9" from the front of the toilet. | 1 | 630
104 | Fairbank Community Center | D. Toilet Compartment | N. Non-compliant toilet paper dispenser | All Gender Toilet Room by Locker Rooms (West Side) | 1 | N/A | Priority 3 | Additional Access | Relocate toilet paper so that it is 24" min. high, located under the grab bar, and between 7" and 9" from the front of the toilet. | 1 | 256
105 | Fairbank Community Center | D. Toilet Compartment | Q. Clearance at toilet < 72" clear depth (MAAB) | Pool - Men's Locker Room | 1 | N/A | Priority 3 | Additional Access | Provide a wheelchair accessible compartment that is 60" wide and 72" deep. | 1 | 6182
106 | Fairbank Community Center | D. Toilet Compartment | R. Coat hook > 48" | Pool - Women’s Locker Room | 1 | N/A | Priority 3 | Additional Access | Lower coat hook so that it is no higher than 48". | 1 | 150
107 | Fairbank Community Center | E. Urinal | A. Rim > 17" high B. Clear floor space not provided at urinal | Men’s/Boys' Toilet Room by Human Resources | 1 | N/A | Priority 1 | Program Access | Provide at least one urinal with the rim no higher than 17" above the finished floor. Remove partition to provide a 30" min. by 48" min. clear floor space positioned for a forward approach. | 1 | 3601
108 | Fairbank Community Center | E. Urinal | A. Rim > 17" high C. Flush control too high or not properly located | All Gender Toilet Room by Locker Rooms (East Side) | 1 | N/A | Priority 1 | Program Access | Provide at least one urinal with the rim no higher than 17" above the finished floor. Mount flush control at 44" max. above the finished floor. | 1 | 3622
109 | Fairbank Community Center | F. Dispensers | A. Controls > 42" high B. Clear floor space not provided at accessory | Pool - Men's Locker Room | 1 | N/A | Priority 3 | Additional Access | Relocate one hand dryer so the operable part is 42" max. above the finished floor and there is a 30" min. by 48" min. clear floor space. | 1 | 256
110 | Fairbank Community Center | F. Dispensers | A. Controls > 42" high B. Clear floor space not provided at accessory | Pool - Women’s Locker Room | 1 | N/A | Priority 3 | Additional Access | Relocate one hand dryer so the operable part is 42" max. above the finished floor and there is a 30" min. by 48" min. clear floor space. | 1 | 256
111 | Fairbank Community Center | F. Dispensers | A. Controls > 42" high D. Dispenser acts as a protruding object | All Gender Toilet Room by Locker Rooms (East Side) | 1 | N/A | Priority 3 | Additional Access | Relocate paper towel dispenser so the operable part is 42" max. above the finished floor, and out of the circulation path. | 1 | 256
112 | Fairbank Community Center | F. Dispensers | A. Controls > 42" high D. Dispenser acts as a protruding object | Men’s/Boys' Toilet Room by Human Resources | 1 | N/A | Priority 3 | Additional Access | Relocate paper towel dispenser so the operable part is 42" max. above the finished floor, and out of the circulation path. | 1 | 353
113 | Fairbank Community Center | F. Dispensers | A. Controls > 42" high D. Dispenser acts as a protruding object | Senior Center, Women's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate paper towel dispenser so the operable part is 42" max. above the finished floor, and out of the circulation path. | 1 | 256
114 | Fairbank Community Center | G. Shower Compartment | U. Accessible shower not provided | Pool - Women’s Showers | 1 | N/A | Priority 1 | Program Access | Provide at least one accessible transfer shower with compliant grab bars and a padded seat. | 1 | 6072
115 | Fairbank Community Center | B. Toilet Compartment (Children) | N. Flush control not on open side R. Non-compliant toilet paper dispenser | Men’s/Boys' Toilet Room by Human Resources | 1 | N/A | Priority 3 | Additional Access | Provide the flush control on the open side of the toilet (transfer side), no higher than 44". Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars. | 1 | 630
116 | Fairbank Community Center | B. Toilet Compartment (Children) | R. Non-compliant toilet paper dispenser U. Coat hook not within reach range | Women's/ Girls' Toilet Room by Human Resources | 1 | 30 | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars. Lower hook so that it is no higher than 36" high for children ages 3-4. | 1 | 406
117 | Fairbank Community Center | D. Dispensers (Children) | A. Dispenser controls > 42" high D. Dispenser is a protruding object | Men’s/Boys' Toilet Room by Human Resources | 1 | N/A | Priority 3 | Additional Access | Relocate paper towel dispenser so the operable part is 42" max. above the finished floor, and out of the circulation path. | 1 | 353
118 | Fairbank Community Center | A. Drinking Fountains | H. No drinking fountain provided for standing users | Meeting Room by Pool | 1 | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users. | 1 | 4028
119 | Fairbank Community Center | A. Drinking Fountains | H. No drinking fountain provided for standing users | Senior Center, Drinking Fountain Next to Toilet Rooms | 1 | N/A | Priority 1 | Program Access | Install a Hi-Lo drinking fountain. | 1 | 4216
120 | Fairbank Community Center | A. Drinking Fountains | J. No drinking fountain provided for seated users | Concession Stand | Exterior | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for seated users. | 1 | 4028
121 | Fairbank Community Center | A. Drinking Fountains | J. No drinking fountain provided for seated users K. Standing height fountain does not have cane protection | Drinking Fountain at Concession Stand (Interior of Fence) | Exterior | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for seated users. Provide a cane-detectable barrier skirt under the high unit. | 1 | 4918
122 | Fairbank Community Center | B. Sink | B. Toe and knee clearances not provided C. Rim or counter > 34" | Teen Room | 1 | N/A | Priority 1 | Program Access | Ensure there is a 27" knee clearance positioned for a forward approach. Relocate sink with the front of the rim or counter no higher than 34". | 1 | 4780
123 | Fairbank Community Center | C. Field | B. Accessible spaces not provided at sidelines seating | Open Field | Exterior | N/A | Priority 1 | Program Access | Provide a 36" x 48" clear floor space at sidelines seating on each side of the bleachers. (Cost estimate for two 3' x 4' asphalt areas.) | 2 | 240
124 | Fairbank Community Center | D. Court | B. Accessible spaces are not provided at sidelines seating | Volleyball Court | Exterior | N/A | Priority 1 | Program Access | Provide a 36" x 48" clear floor space at sidelines seating on each side of the bleachers. (Cost estimate for two 3' x 4' concrete areas.) | 2 | 384
125 | Fairbank Community Center | D. Court | C. Court is not connected to an accessible route | Gaga Ball Court | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the court and an ADA compliant doorway to the court. (Cost estimate for a hinged doorway at court and 10' long 4' wide asphalt route to the court.) | 1 | 750
126 | Fairbank Community Center | N/A | N/A | Pool - Main Entrance | 1 | N/A |  |  | This is a good example of a recessed floor mat. | 1 | 0
127 | Fairbank Community Center | N/A | N/A | Pre-school Multipurpose Room | 1 | N/A | Priority 4 | Enhanced Usability | For children aged 3-4 under the ADA the recommendations for reach ranges are between 20" and 36" high, and this blackboard is located near the top of that reach range at 33" above the finished floor. Recommend providing a lower blackboard. | 1 | 0
128 | Fairbank Community Center | N/A | N/A | Senior Center, Podium | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing an adjustable height podium. | 1 | 0
129 | Fairbank Community Center | N/A | N/A | Kids Summer Camp Picnic Area | Exterior | N/A |  |  | This is a good example of an accessible picnic table. | 1 | 0
130 | Fairbank Community Center | N/A | N/A | Pool - Main Entrance | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend applying glass manifestation to large expanse of clear glass, in order to make the glass visible, preventing injury through collision. | 1 | 0
1 | Fire Department Station 1 | G. Entrance | L. Surface not stable, firm, and slip-resistant at entrance | Secondary Entrance on South | Exterior | N/A | Priority 3 | Additional Access | Remove the weeds from the door maneuvering clearance area. | 1 | 0
2 | Fire Department Station 1 | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Main Entrance | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
3 | Fire Department Station 1 | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Apparatus Room, South Side Exit | LL | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
4 | Fire Department Station 1 | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Apparatus Room, North Side Exit (Front) | LL | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
5 | Fire Department Station 1 | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) R. Door requires > 15 lbs. of force to open | Secondary Entrance on South | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. Adjust closers of exterior doors so doors do not require more than 15 pounds of force. | 1 | 432
6 | Fire Department Station 1 | H. Emergency Exit | P. Threshold > 1/2" high | Apparatus Room, South Side Exit | Exterior | N/A | Priority 3 | Additional Access | Alter the threshold to be 1/2" high max. | 1 | 150
7 | Fire Department Station 1 | H. Emergency Exit | P. Threshold > 1/2" high | Apparatus Room, North Side Exit (Front) | Exterior | N/A | Priority 3 | Additional Access | Alter the threshold to be 1/2" high max. | 1 | 150
8 | Fire Department Station 1 | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Conference Room | 1 | N/A | Priority 3 | Additional Access | Relocate the chair to ensure that there is 18" clear on the latch side of the door. | 1 | 0
9 | Fire Department Station 1 | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Men’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Provide an automatic door opener. | 1 | 3060
10 | Fire Department Station 1 | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Secondary Entrance/ Egress | 1 | N/A | Priority 3 | Additional Access | Ensure that vending machine is placed so that it does not affect clear width or maneuvering clearance at the door. | 1 | 0
11 | Fire Department Station 1 | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Women’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Provide an automatic door opener. | 1 | 3060
12 | Fire Department Station 1 | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign G. Sign not located on the latch side of the door | Shift Commander's Office | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. Locate sign at permanent rooms alongside the door on the latch side. | 1 | 232
13 | Fire Department Station 1 | J. Service Counter | B. Counter > 36" high | Reception/ Chief's Secretary | 1 | N/A | Priority 3 | Additional Access | Provide a counter that is 36" max. above the ground or finished floor. | 1 | 880
14 | Fire Department Station 1 | A. Overall Access | A. Not on an accessible route | Apparatus Room | LL | N/A | Priority 1 | Program Access | There is no accessible route (only stairs) between the apparatus room and the toilet rooms. It may be technically infeasible to create an accessible route. | 1 | 0
15 | Fire Department Station 1 | B. Lavatory | B. Toe or knee clearances not provided E. Plumbing underneath is exposed G. Dispensers not within reach range | Women’s Toilet Room | 1 | N/A | Priority 1 | Program Access | Provide at least one lavatory with knee and toe clearance positioned for a forward approach. Insulate or otherwise configure pipes to prevent contact at the lavatory. Lower the paper towel dispenser to 42" max. above the floor. | 1 | 2131
16 | Fire Department Station 1 | B. Lavatory | B. Toe or knee clearances not provided E. Plumbing underneath is exposed G. Dispensers not within reach range | Men’s Toilet Room | 1 | N/A | Priority 1 | Program Access | Provide at least one lavatory with knee and toe clearance positioned for a forward approach. Insulate or otherwise configure pipes to prevent contact at the lavatory. Lower the paper towel dispenser to 42" max. above the floor. | 1 | 2131
17 | Fire Department Station 1 | C. Single-User Toilet | B. Flush control not on open side | Women’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate the flush control to the open side. | 1 | 374
18 | Fire Department Station 1 | C. Single-User Toilet | O. Hook located > 48" high | Women’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Locate hook no higher than 48" above the finished floor. | 1 | 150
19 | Fire Department Station 1 | A. Drinking Fountains | H. No drinking fountain provided for standing users | Corridor by Toilet Rooms | 1 | N/A | Priority 1 | Program Access | Install a Hi-Lo drinking fountain. | 1 | 4216
20 | Fire Department Station 1 | N/A | A. Signage is not provided | Conference Room | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing designation signage with raised characters and braille at all permanent rooms where signage is not provided. | 1 | 0
21 | Fire Department Station 1 | N/A | A. Signage is not provided | Reception/ Chief's Secretary | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing designation signage with raised characters and braille at all permanent rooms where signage is not provided. | 1 | 0
1 | Fire Department Station 2 | N/A | N/A | Main Entrance | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing signage with contact information regarding the fire department and the location of services that is open to the public on a sign that is located on an accessible route. | 1 | 0
2 | Fire Department Station 2 | N/A | N/A | Main Entrance | Exterior | N/A |  |  | If the Town of Sudbury is planning to open this facility to the public in the future, the 3-inch change in level at the entrance will need to be renovated. | 1 | 0
1 | Fire Department Station 3 | A. Exterior Access Route | J. Level changes > 1/4" | Main Entrance Walkway | Exterior | N/A | Priority 1 | Program Access | Alter change in level to be 1/4" high max. (See ID #2 for cost.) | 1 | 0
2 | Fire Department Station 3 | G. Entrance | O. Threshold > 1/2" high Q. Hardware not operable with a closed fist | Main Entrance | Exterior | N/A | Priority 1 | Program Access | Alter threshold to be 1/2" high max. Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. (Cost estimate is for compliant hardware and providing a level (2% slope max.) concrete 60" wide by 60" deep area at the door and a sloped walkway (max. slope of 8.33%) to the landing.) | 1 | 1204
3 | Fire Department Station 3 | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Main Entrance | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 1116
4 | Fire Department Station 3 | H. Emergency Exit | G. Maneuvering clearance(s) not provided L. Mat not securely attached | Main Entrance | 1 | N/A | Priority 3 | Additional Access | Provide an automatic door opener. Secure the mat. | 1 | 3060
1 | Flynn Building | C. Off-Street Parking Lot or Garage | O. Sign does not have the designation "Van Accessible" | Accessible Parking Spots | Exterior | N/A | Priority 1 | Program Access | Add the designation "Van Accessible" to one of the two accessible parking spaces by the building entrance. | 1 | 500
2 | Flynn Building | G. Entrance | B. Entrance not on an accessible route C. Directional sign to accessible entrance not provided | Inaccessible Entrance at South Stair | G | N/A | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible entrance. | 1 | 346
3 | Flynn Building | G. Entrance | D. International Symbol of Accessibility not provided | Accessible Entrance at North Stair | G | N/A | Priority 1 | Program Access | Provide a sign with the International Symbol of Accessibility (ISA). | 1 | 346
4 | Flynn Building | G. Entrance | M. Mat not securely attached | Accessible Entrance at North Stair | G | N/A | Priority 1 | Program Access | Secure the mat. | 1 | 0
5 | Flynn Building | H. Emergency Exit | B. Tactile sign not provided at exit | South Stair Exit | G | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. | 1 | 232
6 | Flynn Building | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | North Stair (Accessible) Exit | G | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
7 | Flynn Building | B. Interior Access Route | B. Obstructed by protruding objects | Corridor | 1 | N/A | Priority 3 | Additional Access | Relocate red box out of the circulation path. | 1 | 0
8 | Flynn Building | B. Interior Access Route | B. Obstructed by protruding objects | Men’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate paper towel dispenser out of the circulation route and the door maneuvering clearance. | 1 | 256
9 | Flynn Building | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Treasurer/ Tax Collector and Accounting | 1 | N/A | Priority 3 | Additional Access | Secure mat. | 1 | 0
10 | Flynn Building | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Selectmen’s/Town Manager Office Counter | 2 | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
11 | Flynn Building | C. Doors, Doorways, & Gates | A. Clear width at door < 32" | Information Systems | 1 | N/A | Priority 3 | Additional Access | Install offset hinges to ensure that the door has a clear width of 32 inches. | 1 | 2232
12 | Flynn Building | C. Doors, Doorways, & Gates | A. Clear width at door < 32" L. Hardware not operable with a closed fist | Single-User Toilet Room | 2 | N/A | Priority 3 | Additional Access | Widen the door so that there is 32" min. clear width. Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. (Cost is included in Toilet Room record, ID # 55.) | 1 | 0
13 | Flynn Building | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Women’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Provide an automatic door opener. | 1 | 3060
14 | Flynn Building | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Human Resources (West Office) Path to Human Resources & Assistant Town Manager | 2 | N/A | Priority 3 | Additional Access | Relocate file cabinet to provide 60" deep of maneuvering clearance at door. | 1 | 0
15 | Flynn Building | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided L. Hardware not operable with a closed fist M. Door requires > 5 lbs. of force to open | Access to Selectmen’s and Town Manager’s Office | 2 | N/A | Priority 3 | Additional Access | Relocate furniture out of the required 18" maneuvering clearance on the latch side of the door. Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. Adjust closers so doors do not require more than 5 pounds of force to open. | 1 | 484
16 | Flynn Building | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Women’s Toilet Room | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
17 | Flynn Building | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Assessors Office | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
18 | Flynn Building | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Information Systems | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
19 | Flynn Building | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Small Meeting Room/ Thompson Conference Room | 2 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
20 | Flynn Building | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Selectmen, Town Manager, Town Counsel and Notary Office | 2 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
21 | Flynn Building | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Large Meeting Room | 2 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
22 | Flynn Building | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Human Resources and Assistant Town Manager Entrance | 2 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
23 | Flynn Building | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Human Resources (West Office) | 2 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
24 | Flynn Building | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Human Resources (East Office) | 2 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
25 | Flynn Building | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Assistant Town Manager | 2 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
26 | Flynn Building | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Planning & Community Development | 2 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
27 | Flynn Building | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Community Housing Coordinator | 2 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
28 | Flynn Building | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Credit Union | 2 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
29 | Flynn Building | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist M. Door requires > 5 lbs. of force to open | Men’s Toilet Room | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. Adjust closers so doors do not require more than 5 pounds of force to open. | 1 | 484
30 | Flynn Building | C. Doors, Doorways, & Gates | M. Door requires > 5 lbs. of force to open | First Floor Entrance on North Side | 1 | N/A | Priority 3 | Additional Access | Adjust closers so doors do not require more than 5 pounds of force to open. | 1 | 0
31 | Flynn Building | G. Elevator | P. Audible car position indicators not provided | Elevator |  | N/A | Priority 3 | Additional Access | Install audible car position indicators. | 1 | 1700
32 | Flynn Building | H. Signage | A. Signage is not provided B. Raised characters not provided on sign D. Braille not provided on sign | North Stair by Assessors Office | 1 | N/A | Priority 1 | Program Access | Locate compliant signage alongside the door on the latch side. Provide text with raised characters duplicated in braille on sign. | 1 | 232
33 | Flynn Building | H. Signage | A. Signage is not provided B. Raised characters not provided on sign D. Braille not provided on sign | South Stair Exit | 1 | N/A | Priority 1 | Program Access | Locate compliant signage alongside the door on the latch side. Provide text with raised characters duplicated in braille on sign. | 1 | 232
34 | Flynn Building | H. Signage | A. Signage is not provided B. Raised characters not provided on sign D. Braille not provided on sign | South Stair | 2 | N/A | Priority 1 | Program Access | Locate compliant signage alongside the door on the latch side. Provide text with raised characters duplicated in braille on sign. | 1 | 232
35 | Flynn Building | H. Signage | A. Signage is not provided B. Raised characters not provided on sign D. Braille not provided on sign | North Stair | 2 | N/A | Priority 1 | Program Access | Locate compliant signage alongside the door on the latch side. Provide text with raised characters duplicated in braille on sign. | 1 | 232
36 | Flynn Building | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Small Meeting Room/ Thompson Conference Room | 2 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
37 | Flynn Building | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Town Counsel | 2 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
38 | Flynn Building | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Large Meeting Room | 2 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
39 | Flynn Building | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Credit Union | 2 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
40 | Flynn Building | H. Signage | G. Sign not located on the latch side of the door | Entrance to Assessors | 1 | N/A | Priority 2 | Navigational Issue | Locate sign at permanent rooms alongside the door on the latch side. | 1 | 0
41 | Flynn Building | H. Signage | G. Sign not located on the latch side of the door | Information Systems | 1 | N/A | Priority 2 | Navigational Issue | Locate sign at permanent rooms alongside the door on the latch side. | 1 | 0
42 | Flynn Building | H. Signage | G. Sign not located on the latch side of the door | Single-User Toilet Room | 2 | N/A | Priority 2 | Navigational Issue | Locate sign at permanent rooms alongside the door on the latch side. | 1 | 0
43 | Flynn Building | H. Signage | H. Non glare finish and contrast not provided on sign | North and South Entrances | Exterior | N/A | Priority 2 | Navigational Issue | Install a sign with a non-glare finish with characters that have a high contrast to the background. | 2 | 464
44 | Flynn Building | H. Signage | Z. Clear floor space not provided at sign | Selectmen, Town Manager, Town Counsel and Notary Office | 2 | N/A | Priority 2 | Navigational Issue | Relocate furniture so that there is a clear floor space of 18" min. by 18" min. centered on the tactile characters at the tactile sign. | 1 | 0
45 | Flynn Building | J. Service Counter | B. Counter > 36" high | Assessors Office | 1 | N/A | Priority 3 | Additional Access | Provide a counter that is 36" max. above the ground or finished floor. | 1 | 880
46 | Flynn Building | J. Service Counter | B. Counter > 36" high | Treasurer/ Tax Collector and Accounting | 1 | N/A | Priority 3 | Additional Access | Provide a counter that is 36" max. above the ground or finished floor. | 1 | 880
47 | Flynn Building | K. Operable Parts | C. Reach < 15" or > 48"(forward/side approach) | First Aid Kit by Women's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate first aid kit so that controls are between no higher than 48" max. above the finished floor. | 1 | 0
48 | Flynn Building | K. Operable Parts | C. Reach < 15" or > 48"(forward/side approach) | Small Meeting Room/ Thompson Conference Room | 2 | N/A | Priority 3 | Additional Access | Provide a a coat hook at 48" max. above the finished floor. | 1 | 150
49 | Flynn Building | K. Operable Parts | C. Reach < 15" or > 48"(forward/side approach) | Planning & Community Development | 2 | N/A | Priority 3 | Additional Access | Provide one coat hook no higher than 48" max. above the finished floor. | 1 | 150
50 | Flynn Building | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Corridor by Elevator | 1 | N/A | Priority 1 | Program Access | Provide at least 1 work surface with 27" min. knee and toe clearance. | 1 | 700
51 | Flynn Building | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Corridor by Treasurer/ Tax Collector and Accounting | 1 | N/A | Priority 1 | Program Access | Provide at least 1 work surface with 27" min. knee and toe clearance. | 1 | 700
52 | Flynn Building | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Selectmen’s Office | 2 | N/A | Priority 1 | Program Access | Provide at least 1 work surface with toe clearance. | 1 | 700
53 | Flynn Building | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Town Manager’s Office | 2 | N/A | Priority 1 | Program Access | Provide at least 1 work surface with 27" min. knee and toe clearance. | 1 | 700
54 | Flynn Building | N. Assembly Area | P. Assistive listening devices not provided | Large Meeting Room | 2 | N/A | Priority 1 | Program Access | If audible communication is integral to the use of the space, provide an assistive listening system. | 1 | 1214
55 | Flynn Building | A. Overall Access | B. Turning space not provided C. Accessible plumbing fixtures or stalls not provided Z. Grab bars not provided | Single-User Toilet Room | 2 | N/A | Priority 1 | Program Access | Renovate and enlarge toilet room or add an accessible single-user toilet room on this floor. | 1 | 24604
56 | Flynn Building | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Women’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
57 | Flynn Building | D. Toilet Compartment | H. Side grab bar < 42" long Q. Clearance at toilet < 72" clear depth (MAAB) Z. Toilet lacks 42" min. clear in front of toilet (MAAB) | Men’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Provide a side wall grab bar that is 42" long min. located 12" max. from the rear wall. Toilet compartment size complies with ADA but not 521 CMR (MAAB). If a variance was not sought during the time of construction, relocate toilet to adjacent wall to ensure that there is 72" min. deep at toilet and 42" min. clear in front of the toilet. (Cost is for grab bar only.) | 1 | 898
58 | Flynn Building | D. Toilet Compartment | T. Centerline < or > 18" (MAAB) | Women’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate toilet so the centerline is 18" from the side wall. | 1 | 2828
59 | Column1: Flynn Building; Column2: N/A; Column3: N/A; Column4: Elevator; Column6: N/A; Column9: Elevator panel signage is clear and well done.; Column10: 1; Column11: 0
60 | Flynn Building | N/A | N/A | Entrance to Women’s Toilet Room | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing additional lighting in the men's and women's toilet room vestibules. | 1 | 0
61 | Flynn Building | N/A | N/A | Assistant Town Manager | 2 | N/A | Priority 4 | Enhanced Usability | Recommend providing signage with raised characters and braille at rooms where signage is not provided. | 1 | 0
62 | Flynn Building | N/A | N/A | Accessible Entrance Walkway | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing edge protection on the side of the sloped walkway. | 1 | 0
63 | Flynn Building | N/A | N/A | Accessible Entrance Stairs | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing handrails at exterior stairs. | 1 | 0
64 | Flynn Building | N/A | N/A | Elevator | G | N/A |  |  | It is encouraging to see directional signs with raised characters and braille. | 1 | 0
1 | Goodnow Library | A. Exterior Access Route | E. Obstructed by protruding objects | Main Entrance Walkway | Exterior | N/A | Priority 1 | Program Access | Provide cane-detectable stanchions with a lower stanchion belt that is cane-detectable, located lower than 27" above the ground. (Cost estimate for 10 stanchions.) | 1 | 870
2 | Goodnow Library | A. Exterior Access Route | N. Accessible route not provided | Main Entrance Bike Rack | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided. (Cost estimate for a 6' long, 4' wide asphalt route.) | 1 | 240
3 | Goodnow Library | B. Curb Ramp | A. Curb ramp not provided | Front of Building | Exterior | N/A | Priority 1 | Program Access | Provide a curb ramp at intersection. (Cost estimate for a concrete curb ramp.) | 1 | 2800
4 | Goodnow Library | C. Off-Street Parking Lot or Garage | E. Van space < 132" or <96" wide | Parking - Side Aisle | Exterior | N/A | Priority 1 | Program Access | Space with van accessible signage is not large enough to be a van accessible parking space. Relocate sign to accessible parking space in center aisle with the 81" wide access aisle. | 1 | 0
5 | Goodnow Library | C. Off-Street Parking Lot or Garage | N. Sign not provided P. Sign bottom < 60" above finished grade | Parking - Center Aisle | Exterior | N/A | Priority 1 | Program Access | Provide two additional accessible parking signs with the bottom of the sign 60" min. above the ground and the top 96" max. above the ground. Relocate existing two signs so that the bottom of the sign is 60" min. above the ground. | 2 | 1000
6 | Goodnow Library | G. Entrance | M. Mat not securely attached | Main Entrance | 1 | N/A | Priority 1 | Program Access | Secure the mat. | 1 | 0
7 | Goodnow Library | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided | Egress Door 2 on Northeast Side | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. | 1 | 464
8 | Goodnow Library | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided | Stairs by Children’s Reading Room | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. | 1 | 464
9 | Goodnow Library | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Main Entrance | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
10 | Goodnow Library | H. Emergency Exit | L. Mat not securely attached | Reading Court | 1 | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
11 | Goodnow Library | B. Interior Access Route | B. Obstructed by protruding objects | Main Library Entrance Gallery | 1 | N/A | Priority 3 | Additional Access | Relocate the defibrillator out of the circulation path. | 1 | 256
12 | Goodnow Library | B. Interior Access Route | B. Obstructed by protruding objects | Main Library Entrance Gallery | 1 | N/A | Priority 3 | Additional Access | Relocate the defibrillator out of the circulation path. | 1 | 256
13 | Goodnow Library | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Children’s Reading Room | 1 | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
14 | Goodnow Library | C. Doors, Doorways, & Gates | D. Maneuvering clearance not provided at recess > 6” | Conference Room | 2 | N/A | Priority 3 | Additional Access | Install an automatic door opener. | 1 | 3060
15 | Goodnow Library | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Children’s Library Entrance | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. Ensure that a clear floor space of 18" by 18" is centered on the tactile characters. | 1 | 232
16 | Goodnow Library | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Children’s Reading Room | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
17 | Goodnow Library | H. Signage | G. Sign not located on the latch side of the door | Egress to Stairs Near Restrooms | 1 | N/A | Priority 2 | Navigational Issue | Locate sign at permanent rooms alongside the door on the latch side. | 1 | 0
18 | Goodnow Library | H. Signage | Z. Signage lacks clear floor space | Quiet Study Rooms | 2 | N/A | Priority 2 | Navigational Issue | Relocate the table to ensure that a clear floor space of 18" by 18" is centered on the tactile characters. | 1 | 0
19 | Goodnow Library | K. Operable Parts | C. Reach < 15" or > 48"(forward/side approach) | Main Entrance Door Bell | 1 | N/A | Priority 3 | Additional Access | Relocate door bell at 48" max. above the ground. | 1 | 138
20 | Goodnow Library | K. Operable Parts | C. Reach < 15" or > 48"(forward/side approach) | Main Entrance to Community Meeting Room | 1 | N/A | Priority 3 | Additional Access | Ensure that one of each type of form is available no higher than 48" above the finished floor. | 1 | 0
21 | Goodnow Library | K. Operable Parts | C. Reach < 15" or > 48"(forward/side approach) | Community Meeting Room | 1 | N/A | Priority 3 | Additional Access | Provide a clothing rack that is located no higher than 48" above the finished floor. | 1 | 92
22 | Goodnow Library | K. Operable Parts | C. Reach < 15" or > 48"(forward/side approach) | Children’s Reading Room | 1 | N/A | Priority 3 | Additional Access | Relocate one hook to be 48" max. above the finished floor. | 1 | 256
23 | Goodnow Library | K. Operable Parts | C. Reach < 15" or > 48"(forward/side approach) | Conference Room | 2 | N/A | Priority 3 | Additional Access | Provide a clothing rack that is located no higher than 48" above the finished floor. | 1 | 92
24 | Goodnow Library | K. Operable Parts | C. Reach < 15" or > 48"(forward/side approach) | Main Entrance Ballot Box | Exterior | N/A | Priority 3 | Additional Access | As the ballot box is out of reach range, ensure there are policies in place to assist voters with disabilities. | 1 | 0
25 | Goodnow Library | L. Children's Reach Ranges | A. 30" x 48" clear space not provided C. Reach < 20" or > 36" (Ages 3 - 4) D. Reach < 18" or > 40" (Ages 5 - 8) E. Reach < 16" or > 44" (Ages 9 - 12) | Children’s Library Seating Area | 1 | N/A | Priority 3 | Additional Access | Provide a 30" min. by 48" min. clear floor space at coat hook. Relocate bin. If used by children 3-4 years old, locate one hook 36" max. above the finished floor. If used by children 5-8 years old, locate one hook 40" max. above the finished floor. If used by children 9-12 years old, locate one hook 44" max. above the finished floor. | 1 | 70
26 | Goodnow Library | L. Children's Reach Ranges | A. 30" x 48" clear space not provided C. Reach < 20" or > 36" (Ages 3 - 4) D. Reach < 18" or > 40" (Ages 5 - 8) E. Reach < 16" or > 44" (Ages 9 - 12) | Children's Library Near Program Room Storytelling | 1 | N/A | Priority 3 | Additional Access | Locate one hook with a 30" by 48" clear floor space. If used by children 3-4 years old, locate one hook 36" max. above the finished floor. If used by children 5-8 years old, locate one hook 40" max. above the finished floor. If used by children 9-12 years old, locate one hook 44" max. above the finished floor. | 1 | 70
27 | Goodnow Library | M. Dining or Work Surfaces | B. At least one or 5% accessible tables not provided C. Knee or toe clearance not provided | Reading Area - Front of Building | 2 | N/A | Priority 1 | Program Access | Provide at least 1 work surface with 27" min. knee and toe clearance. | 1 | 700
28 | Goodnow Library | M. Dining or Work Surfaces | B. At least one or 5% accessible tables not provided C. Knee or toe clearance not provided D. Top of dining/work surface < 28" or > 34" | Sara Sherman Now Lab | 2 | N/A | Priority 1 | Program Access | Provide at least one work surface with top between 28"- 34" above the floor and 27" clear height underneath. | 1 | 700
29 | Goodnow Library | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Main Library Near Children’s Library Entrance (New Books) | 1 | N/A | Priority 1 | Program Access | Table lacks toe clearance. Provide at least work surface with toe clearance in this area. | 1 | 700
30 | Goodnow Library | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Desktop Near Shelves | 2 | N/A | Priority 1 | Program Access | Provide at least 1 work surface with 27" min. knee and toe clearance. | 1 | 700
31 | Goodnow Library | M. Dining or Work Surfaces | D. Top of dining/work surface < 28" or > 34" | Main Library New Book Area Near Open Stair |  | N/A | Priority 3 | Additional Access | Provide at least one work surface in this area with the top between 28"- 34" above the floor and 27" clear height underneath. | 1 | 700
32 | Goodnow Library | M. Dining or Work Surfaces | D. Top of dining/work surface < 28" or > 34" | Computer Near Large Print Books - Main Library | 1 | N/A | Priority 3 | Additional Access | Provide at least work surface with top between 28"- 34" above the floor and 27" clear height underneath. | 1 | 700
33 | Goodnow Library | S. Picnic Tables | C. At least 5% accessible spaces not provided F. 30" clear width not provided G. Toe or knee clearance at tables not provided | Reading Court | Exterior | N/A | Priority 1 | Program Access | Provide at least 1 accessible dining surface with a 30" wide by 48" deep clear floor space. Ensure the surface has the required toe and knee clearance. | 1 | 1400
34 | Goodnow Library | B. Lavatory | F. Mirror above lavatory w/reflective surface > 40" | All-Gender Toilet Room East of Drinking Fountain | 2 | N/A | Priority 3 | Additional Access | Lower mirror so that the bottom surface is at 40" max. above the finished floor. | 1 | 256
35 | Goodnow Library | C. Single-User Toilet | O. Hook located > 48" high | All-Gender Toilet Room - Children’s Library | 1 | N/A | Priority 3 | Additional Access | Locate hook no higher than 48" above the finished floor. | 1 | 150
36 | Goodnow Library | C. Single-User Toilet | O. Hook located > 48" high | All-Gender Toilet Room East of Drinking Fountain | 2 | N/A | Priority 3 | Additional Access | Locate hook no higher than 48" above the finished floor. | 1 | 150
37 | Goodnow Library | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge R. Coat hook > 48" | Women's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Repair hinge. Lower coat hook so that it is no higher than 48". | 1 | 150
38 | Goodnow Library | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge R. Coat hook > 48" | Men's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Repair hinge. Lower coat hook so that it is no higher than 48". | 1 | 150
39 | Goodnow Library | E. Urinal | C. Flush control too high or not properly located | Men's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Mount flush control at 44" max. above the finished floor. | 1 | 374
40 | Goodnow Library | F. Dispensers | A. Controls > 42" high | Women's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate the paper towel dispenser so the operable part is 42" max. above the finished floor. | 1 | 353
41 | Goodnow Library | F. Dispensers | A. Controls > 42" high | Men's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate the paper towel dispenser so the operable part is 42" max. above the finished floor. | 1 | 353
42 | Goodnow Library | F. Dispensers | A. Controls > 42" high | All-Gender Toilet Room East of Drinking Fountain | 2 | N/A | Priority 3 | Additional Access | Relocate paper towel dispenser so the operable part is 42" max. above the finished floor. | 1 | 353
43 | Goodnow Library | C. Lavatory (Children) | A. Toe or knee clearances not provided F. Mirror above lavatory w/reflective surface > 31" | All-Gender Toilet Room - Children’s Library | 1 | N/A | Priority 1 | Program Access | Provide at least one lavatory with 25" min. knee clearance positioned for a forward approach. Ensure toe clearance is also provided. Lower mirror so that the bottom surface is at 31" above finished floor. | 1 | 1942
44 | Goodnow Library | A. Drinking Fountains | H. No drinking fountain provided for standing users | Fountain Near Toilet Rooms | 1 | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users. | 1 | 4028
45 | Goodnow Library | A. Drinking Fountains | H. No drinking fountain provided for standing users | Fountain Near Toilet Room in Children’s Library | 1 | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users. | 1 | 4028
46 | Goodnow Library | A. Drinking Fountains | K. Standing height fountain does not have cane protection | Fountain Near All-Gender Toilet Rooms | 2 | N/A | Priority 3 | Additional Access | Provide a cane-detectable barrier skirt under the high unit. | 1 | 890
47 | Goodnow Library | B. Sink | B. Toe and knee clearances not provided | Sara Sherman Now Lab | 2 | N/A | Priority 1 | Program Access | Ensure there is a 27" knee clearance positioned for a forward approach. Brace sink and remove cabinet. | 1 | 1686
48 | Goodnow Library | N/A | N/A | Community Meeting Room | 1 | N/A |  |  | This is a good example of signage for an assistive listening system. | 1 | 0
49 | Goodnow Library | N/A | N/A | Community Meeting Room | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing an adjustable height podium. | 1 | 0
50 | Goodnow Library | N/A | N/A | Egress to Stairs Near Restrooms | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing contrast strips on stair treads. | 1 | 0
51 | Goodnow Library | N/A | N/A | Children’s Library Entrance | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing a large visual sign at the entrance to the children's library. | 1 | 0
52 | Goodnow Library | N/A | N/A | Stairs by Children’s Reading Room | 2 | N/A | Priority 4 | Enhanced Usability | Recommend providing contrast strips on stair treads. | 1 | 0
53 | Goodnow Library | N/A | N/A | Conference Room | 2 | N/A | Priority 4 | Enhanced Usability | Recommend providing a designation sign with raised characters and braille at the engineering conference room. | 1 | 0
54 | Goodnow Library | N/A | N/A | Stair by Front of Library on Southeast Side | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing contrast strips on stair treads. | 1 | 0
1 | Hosmer House | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Sidewalk East of House | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). (Cost estimate for 30' long 4' wide asphalt route.) | 1 | 1200
2 | Hosmer House | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Sidewalk West of Town Hall (Toward Parking Lot) | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). (Cost estimate for 10' long 4' wide asphalt route.) | 1 | 400
3 | Hosmer House | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) M. Route not maintained in operable working condition | Garden Path Behind House | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). Ensure the accessible route is maintained in operable working condition. (Cost estimate for 60' long by 4' wide brick paver walkway.) | 1 | 3440
4 | Hosmer House | A. Exterior Access Route | N. Accessible route not provided | Garden East of Garage | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided to the garden east of the garage and to one bench in this area. (Cost estimate for 6' long 4' wide brick paver walkway.) | 1 | 688
5 | Hosmer House | G. Entrance | B. Entrance not on an accessible route | Main Entrance Hallway | 1 | N/A | Priority 1 | Program Access | The temporary ramp to the main entrance is not compliant for a level change that is greater than 8.5 inches. On occasions when the house is open to the public, IHCD recommends renting an accessible metal portable ramp with compliant handrails and landings and a running slope no greater than 8.33 percent. | 1 | 0
6 | Hosmer House | G. Entrance | B. Entrance not on an accessible route C. Directional sign to accessible entrance not provided E. Clear width at door is < 32" | General Store Entrance | Exterior | N/A | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible entrance. Alteration of the door width may not be feasible. Compliance with the requirements may threaten or destroy the historic significance of the building. | 1 | 346
7 | Hosmer House | G. Entrance | Q. Hardware not operable with a closed fist | General Store Entrance | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
8 | Hosmer House | A. Means of Egress | B. Tactile exit sign not provided | Back Hallway Exit | 1 | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. | 1 | 232
9 | Hosmer House | A. Means of Egress | B. Tactile exit sign not provided | General Store Exit to Concord Road | 1 | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. | 1 | 232
10 | Hosmer House | B. Interior Access Route | A. Route < 36" wide | Dining Room | 1 | N/A | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. Route is allowed to narrow to 32" wide min. for 24" of depth. | 1 | 0
11 | Hosmer House | B. Interior Access Route | A. Route < 36" wide | Dining Room | 1 | N/A | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. Route is allowed to narrow to 32" wide min. for 24" of depth. | 1 | 0
12 | Hosmer House | B. Interior Access Route | A. Route < 36" wide | Dining Room - Route to Kitchen | 1 | N/A | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. Route is allowed to narrow to 32" wide min. for 24" of depth. | 1 | 0
13 | Hosmer House | B. Interior Access Route | B. Obstructed by protruding objects | Doorway From Dining Room to Hallway | 1 | N/A | Priority 3 | Additional Access | Provide a cane-detectable barrier underneath the overhead cabinet. | 1 | 306
14 | Hosmer House | B. Interior Access Route | H. Accessible route not provided | Second Floor | 2 | N/A | Priority 1 | Program Access | Provide a video of the rooms on the second floor or photographs to provide program accessibility. | 1 | 0
15 | Hosmer House | C. Doors, Doorways, & Gates | A. Clear width at door < 32" K. Threshold > 1/2" high | Doorway From Living Room to Dining Room | 1 | N/A | Priority 3 | Additional Access | Provide offset hinges at door to provide 32" min. clear width. The historic hinges of these doors could be retained in storage. Alteration to the threshold may not be feasible. Compliance with the requirements may threaten or destroy the historic significance of the building. Provide a video of the rooms or photographs to provide program accessibility. | 1 | 2232
16 | Hosmer House | C. Doors, Doorways, & Gates | H. Mat not securely attached | Doorway From Dining Room to Kitchen | 1 | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
17 | Hosmer House | C. Doors, Doorways, & Gates | K. Threshold > 1/2" high | Living Room | 1 | N/A | Priority 3 | Additional Access | Alteration may not be feasible. Compliance with the requirements may threaten or destroy the historic significance of the building. Provide a video of the rooms or photographs to provide program accessibility. | 1 | 0
18 | Hosmer House | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Emergency Egress From Back Hallway | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
19 | Hosmer House | J. Service Counter | B. Counter > 36" high | General Store | 1 | N/A | Priority 3 | Additional Access | Provide another table that is 36" max. above the ground or finished floor. | 1 | 500
20 | Hosmer House | A. Overall Access | B. Turning space not provided C. Accessible plumbing fixtures or stalls not provided | Toilet Room | 1 | N/A | Priority 1 | Program Access | As toilet room was renovated in 1983, an accessible toilet room would have been required at the time as part of 521 CMR unless a variance was sought at the time. Recommend providing an accessible toilet room on this level if a toilet room is provided to the public. | 1 | 0
21 | Hosmer House | N/A | N/A | Garden Path Behind House and East of the Garage | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing a level clear floor space of 36" wide min. by 48" deep min. alongside one bench in each garden so that a wheelchair user can sit alongside a person seated on the bench. | 2 | 0
22 | Hosmer House | N/A | N/A | Living Room | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing stanchions that stand out more from the background and are easier to see. | 1 | 0
23 | Hosmer House | N/A | N/A | Garden Path Behind House | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend locating sign regarding the Victorian kitchen garden on an accessible route. | 1 | 0
24 | Hosmer House | N/A | N/A | Stairs Outside of Back Hallway Exit | Exterior | N/A | Priority 4 | Enhanced Usability | Stairs may be hazardous for users. Recommend renovating stairs. | 1 | 0
25 | Hosmer House | N/A | N/A | General Store Entrance | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing handrails on the stairs to the porch. | 1 | 0
26 | Hosmer House | N/A | N/A | General Store Entrance Door Stairs | Exterior | N/A | Priority 4 | Enhanced Usability | Risers and treads are different sizes. It may not be technically feasible to adjust risers or treads, however stairs may be hazardous for users. Recommend providing a railing on at least one side. | 1 | 0
27 | Hosmer House | N/A | N/A | Driveway East of House | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a drop off area in the driveway and allowing visitors who are not able to walk from one of the Town Hall parking lots to park in the driveway. | 1 | 0
28 | Hosmer House | N/A | N/A | Lower Town Hall Parking Lot | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a van accessible parking space in this lot as it is closer to the Hosmer House than the lot behind Town Hall. | 1 | 0
1 | Loring Parsonage | C. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces C. Total # of designated van accessible spaces O. Sign does not have the designation "Van Accessible" E. Van space < 132" or <96" wide H. Access aisle not compliant | Parking Lot | Ext | N/A | Priority 1 | Program Access | Provide at least one van accessible parking space for the facility. (Cost estimate includes "Van Accessible" sign and restriping.) | 1 | 800
2 | Loring Parsonage | G. Entrance | M. Mat not securely attached | Lobby - Northeast Accessible Entrance | 1 | N/A | Priority 1 | Program Access | Secure the mat. | 1 | 0
3 | Loring Parsonage | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided | Stairwell - Exit to East Side of Building | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. | 2 | 464
4 | Loring Parsonage | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided | Exhibit Space - Exit to West Side of Building | 1 | 106 | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. | 2 | 464
5 | Loring Parsonage | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Vestibule - Northeast Accessible Entrance | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
6 | Loring Parsonage | B. Interior Access Route | B. Obstructed by protruding objects | Lobby - Northeast Door to Parking Lot | 1 | N/A | Priority 3 | Additional Access | Provide a cane-detectable barrier under the cabinet. | 1 | 306
7 | Loring Parsonage | B. Interior Access Route | L. Vertical clearance < 80" above finished floor | File Room - East Side of Building | 2 | N/A | Priority 3 | Additional Access | Provide ADA compliant double belt stanchions on each side of the route where the ceiling is less than 80" above the finished floor. Ensure that the lower horizontal belt of the stanchion is 27 inches maximum above the floor. (Cost estimate for 4 stanchions.) | 4 | 372
8 | Loring Parsonage | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | File Room to Research Room | 2 | N/A | Priority 3 | Additional Access | Relocate storage to provide 18" clear on the latch side of the door and at sign. | 1 | 0
9 | Loring Parsonage | C. Doors, Doorways, & Gates | K. Threshold > 1/2" high L. Hardware not operable with a closed fist | Exhibit Space - Southwest Side of Building | 1 | 106 | Priority 3 | Additional Access | Alter the threshold to be 1/2" high max. Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 634
10 | Loring Parsonage | F. Platform Lift or LULA Elevator | G. Doors remain open < 20 seconds | Platform Lift, East Side of Building | 1 | N/A | Priority 3 | Additional Access | Adjust door opening speed. | 1 | 0
11 | Loring Parsonage | F. Platform Lift or LULA Elevator | G. Doors remain open < 20 seconds | Platform Lift, East Side of Building | 2 | N/A | Priority 3 | Additional Access | Adjust door opening speed. | 1 | 0
12 | Loring Parsonage | H. Signage | F. Visual characters < 40" above ground | Platform Lift, East Side of Building | 2 | N/A | Priority 2 | Navigational Issue | Mount visual sign regarding fire precautions so that the baseline of the lowest character is 40" min. above the finished floor. | 1 | 0
13 | Loring Parsonage | J. Service Counter | B. Counter > 36" high | Lobby - East Side of Building | 1 | N/A | Priority 3 | Additional Access | Provide a counter that is 36" max. above the ground or finished floor. | 1 | 880
14 | Loring Parsonage | C. Single-User Toilet | O. Hook located > 48" high | Toilet Room - North Side of Building | 1 | 103 | Priority 3 | Additional Access | Locate hook no higher than 48" above the finished floor. | 1 | 150
15 | Loring Parsonage | N/A | N/A | Platform Lift, East Side of Building | 1 | N/A | Priority 3 | Additional Access | Relocate shelves to provide easier access to and clearance at lift controls. | 1 | 0
16 | Loring Parsonage | N/A | N/A | Exhibit Space - North Side of Building | 1 | 104 | Priority 4 | Enhanced Usability | Recommend providing signage with raised characters and braille at all permanent rooms including the door between Rooms 104 and 105. | 1 | 0
17 | Loring Parsonage | N/A | N/A | Main Entrance - Route to Parking Lot | Ext | N/A | Priority 4 | Enhanced Usability | Recommend providing edge protection along open sides of walkway. | 1 | 0
1 | Parks and Grounds Building | G. Entrance | B. Entrance not on an accessible route E. Clear width at door is < 32" M. Mat not securely attached O. Threshold > 1/2" high Q. Hardware not operable with a closed fist | Entrance to Office on East | Exterior | N/A | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible entrance. Secure the mat. Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 830
2 | Parks and Grounds Building | G. Entrance | D. International Symbol of Accessibility not provided O. Threshold > 1/2" high | East Garage - Building Exit | Exterior | N/A | Priority 1 | Program Access | Install a metal ramp to provide an accessible entry route to the building. After the entrance is made accessible, provide a sign with the International Symbol of Accessibility (ISA). (Cost is for a 7' perforated metal ramp with a 5' x 5' platform courtesy of Amramp and an exterior sign.) | 1 | 3146
3 | Parks and Grounds Building | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided | Office Entrance From East Garage | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. | 1 | 464
4 | Parks and Grounds Building | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | East Garage - Building Exit | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. After the entrance/exit door is brought into compliance, provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
5 | Parks and Grounds Building | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided H. Mat not securely attached L. Hardware not operable with a closed fist | East Garage - Building Exit | 1 | N/A | Priority 1 | Program Access | Relocate the trash bin. Secure the mat. Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
6 | Parks and Grounds Building | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Route to Center Garage From East Garage | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
7 | Parks and Grounds Building | B. Lavatory | A. Not on an accessible route B. Flush control not on open side B. Toe or knee clearances not provided B. Turning space not provided D. Faucet is not operable with a closed fist E. Grab bar not provided E. Plumbing underneath is exposed F. Mirror above lavatory w/reflective surface > 40" G. Dispensers not within reach range | Center Garage Toilet Room | 1 | N/A | Priority 1 | Program Access | Add an accessible single-user toilet room located on an accessible route. | 1 | 24604
8 | Parks and Grounds Building | B. Sink | B. Toe and knee clearances not provided D. Non-compliant faucets G. Dispenser not within reach range | Center Garage | 1 | N/A | Priority 1 | Program Access | Ensure there is a 27" knee clearance positioned for a forward approach. Install faucets that do not require tight grasping, pinching, or twisting of the wrist. Relocate dispenser 48" max. above the finished floor or ground. | 1 | 2928
1 | Police Station | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Lobby Exit | 1 | 104 | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
2 | Police Station | H. Emergency Exit | C. Directional sign to accessible emergency exit not provided | Meeting Room | 1 | 144 | Priority 2 | Navigational Issue | Provide a directional sign indicating the location of the nearest accessible emergency exit. | 1 | 232
3 | Police Station | H. Emergency Exit | R. Door requires > 15 lbs. of force to open | Meeting Room to Parking | 1 | 144 | Priority 3 | Additional Access | Adjust closers of exterior doors so doors do not require more than 15 pounds of force. Note: Fire doors shall have a minimum opening force allowable by the appropriate administrative authority. | 1 | 0
4 | Police Station | K. Operable Parts | C. Reach < 15" or > 48"(forward/side approach) | Meeting Room | 1 | 144 | Priority 3 | Additional Access | Relocate clothes rod to be 48" max. above the finished floor. | 2 | 512
5 | Police Station | N. Assembly Area | P. Assistive listening devices not provided | Meeting Room | 1 | 144 | Priority 1 | Program Access | If audible communication is integral to the use of the space, provide an assistive listening system. | 1 | 1214
6 | Police Station | R. Detention Facilities | C. Side or rear grab bar not provided | Accessible Cell 4 | 1 | 136 | Priority 1 | Program Access | Provide one ligature-resistant grab bar on the side wall of the water closet and one on the rear wall. | 2 | 1796
7 | Police Station | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Men’s Toilet Room by Lobby | 1 | 103 | Priority 3 | Additional Access | Repair hinge. | 1 | 0
8 | Police Station | G. Shower Compartment | E. Grab bars not provided O. Control height < 38" or > 48" | Shower by Booking | 1 | N/A | Priority 1 | Program Access | Provide a ligature resistant grab bar on the control wall and one on the adjacent wall to comply with a roll-in type shower. Relocate controls at 48" max. above the finished floor. | 1 | 2374
9 | Police Station | B. Sink | B. Toe and knee clearances not provided C. Rim or counter > 34" | Meeting Room | 1 | 144 | Priority 1 | Program Access | Relocate sink with the front of the rim or counter no higher than 34". Provide 27" high of knee clearance positioned for a forward approach. | 1 | 4780
10 | Police Station |  |  | Meeting Room | 1 | 144 | Priority 4 | Enhanced Usability | Recommend providing an adjustable height podium. | 1 | 0
1 | Town Hall | C. Off-Street Parking Lot or Garage | E. Van space < 132" or <96" wide O. Sign does not have the designation "Van Accessible" | Parking Lot | Ext | N/A | Priority 1 | Program Access | Provide one van accessible space that is at least 132" wide. Ensure the access aisle is 60" min. for this space. Add the designation "Van Accessible" to the sign located at the van accessible space. (Cost estimate for repainting two spaces, and striping the landing to the ramp to be 60" min, and providing signage with the designation "Van Accessible" at the van accessible parking space.) | 1 | 1100
2 | Town Hall | E. Exterior Ramp | C. Running slope > 1:12 (8.3%) Q. Edge protection < 4" high | Accessible Entrance to Meeting Hall | 1 | N/A | Priority 3 | Additional Access | Reduce running slope to be no steeper than 1:12 (8.3%). Provide edge protection that prevents the passage of a 4" diameter sphere, where any portion of the sphere is within 4" of the finished floor or ground surface. (Cost for repaving a concrete ramp to a shallower slope, including 1-1/2" pipe handrails - per 15 linear feet and providing edge protection at the bottom exterior rail.) | 1 | 6587
3 | Town Hall | E. Exterior Ramp | L. Landing < 60" min. long | East Entrance Ramp | 1 | N/A | Priority 3 | Additional Access | Redo striping in the parking lot to ensure that 60" min. deep is provided at the base of the ramp. (Cost listed under ID #1.) | 1 | 0
4 | Town Hall | G. Entrance | B. Entrance not on an accessible route C. Directional sign to accessible entrance not provided | Entrance to South Stairwell | 1 | N/A | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible entrance. | 1 | 346
5 | Town Hall | G. Entrance | B. Entrance not on an accessible route C. Directional sign to accessible entrance not provided | West Side of Building | Ext | N/A | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible entrance. (Note: Where a directional sign is required, it should be located to minimize backtracking. In some cases, this could mean locating a sign at the beginning of a route, not just at the inaccessible entrance to the building.) | 2 | 692
6 | Town Hall | G. Entrance | M. Mat not securely attached | Lobby From Main Entrance to Meeting Hall | 1 | N/A | Priority 1 | Program Access | Secure the mat. | 1 | 0
7 | Town Hall | G. Entrance | M. Mat not securely attached | Accessible Entrance to Meeting Hall | 1 | N/A | Priority 1 | Program Access | Secure the mat. | 1 | 0
8 | Town Hall | G. Entrance | Q. Hardware not operable with a closed fist | Main Entrance - West Side of Building | Ext | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
9 | Town Hall | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided | Exit From South and North Stairwells | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. | 4 | 928
10 | Town Hall | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided R. Door requires > 15 lbs. of force to open | Main Entrance - West Side of Building | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. Adjust closers of exterior doors so doors do not require more than 15 pounds of force. | 2 | 464
11 | Town Hall | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Exit to East Side of Building | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
12 | Town Hall | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) G. Maneuvering clearance(s) not provided L. Mat not securely attached | Accessible Exit From Meeting Hall | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. Provide an automatic door opener. Secure the mat. | 1 | 3492
13 | Town Hall | B. Interior Access Route | B. Obstructed by protruding objects | Men’s Toilet Room by Lobby at Main Entrance | 1 | N/A | Priority 3 | Additional Access | Provide a cane-detectable barrier at the light fixture. | 1 | 306
14 | Town Hall | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Hallway Between Town Clerk Office and East Side of Building | 1 | N/A | Priority 3 | Additional Access | Secure mat. | 1 | 0
15 | Town Hall | B. Interior Access Route | H. Accessible route not provided | South Stairwell - Entrance to Town Clerk Office | 1 | N/A | Priority 1 | Program Access | There is no interior accessible route to the Town Clerk office. Look into the feasibility of installing a platform lift between the Meeting Hall and this office. | 1 | 21660
16 | Town Hall | B. Interior Access Route | H. Accessible route not provided | South Stairwell | 2 | N/A | Priority 1 | Program Access | At the time of survey, no public programs were provided on the second floor and mezzanine. If public programs will be provided on these levels, consider providing a Limited Use Limited Access (LULA) elevator. | 1 | 0
17 | Town Hall | C. Doors, Doorways, & Gates | H. Mat not securely attached L. Hardware not operable with a closed fist | Hallway Between Town Clerk Office and East Exit | 1 | N/A | Priority 1 | Program Access | Secure the mat. Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
18 | Town Hall | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Meeting Hall Door | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
19 | Town Hall | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Women’s Toilet Room by Lobby at Main Entrance | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
20 | Town Hall | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Men’s Toilet Room by Lobby at Main Entrance | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
21 | Town Hall | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | South Stairwell to Meeting Hall | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
22 | Town Hall | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign F. International Symbol of Acc. not provided G. Sign not located on the latch side of the door | Employee Only Toilet Room - Meeting Hall | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. Provide a sign with the International Symbol of Accessibility. Locate sign at permanent rooms alongside the door on the latch side. | 1 | 232
23 | Town Hall | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign G. Sign not located on the latch side of the door | South Stairwell - Entrance to Town Clerk Office | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. Locate sign at permanent rooms alongside the door on the latch side. | 1 | 232
24 | Town Hall | H. Signage | H. Non glare finish and contrast not provided on sign | Ramp at East Entrance to Town Clerk and Veteran's Services | Ext | N/A | Priority 2 | Navigational Issue | Install a sign with a non-glare finish with characters that have a high contrast to the background. | 1 | 232
25 | Town Hall | J. Service Counter | B. Counter > 36" high | Town Clerk Office | 1 | N/A | Priority 3 | Additional Access | Provide a counter that is 36" max. above the ground or finished floor. | 1 | 880
26 | Town Hall | J. Service Counter | B. Counter > 36" high Z. Knee clearance not compliant | Town Clerk Office | 1 | N/A | Priority 3 | Additional Access | Provide a counter that is 36" max. above the ground or finished floor. Ensure that knee clearance is 17" min. for a forward approach. | 1 | 880
27 | Town Hall | K. Operable Parts | C. Reach < 15" or > 48"(forward/side approach) | Town Clerk Office Brochures | 1 | N/A | Priority 3 | Additional Access | Relocate one of each type of form to be no higher than 48" above the finished floor. | 1 | 0
28 | Town Hall | M. Dining or Work Surfaces | B. At least one or 5% accessible tables not provided C. Knee or toe clearance not provided | Meeting Hall | 1 | N/A | Priority 1 | Program Access | Provide at least 1 work surface with 27" min. knee and toe clearance. | 1 | 700
29 | Town Hall | N. Assembly Area | N. Accessible route to stage not provided | Meeting Hall - Stage | 1 | N/A | Priority 1 | Program Access | Provide a portable ramp to the stage. | 1 | 500
30 | Town Hall | A. Overall Access | H. Audible and visible alarms not provided | Employee Only Toilet Room - Meeting Hall | 1 | N/A | Priority 1 | Program Access | When fire system is updated, ensure that a visible and audible fire alarm is installed. | 1 | 0
31 | Town Hall | B. Lavatory | B. Toe or knee clearances not provided G. Dispensers not within reach range Z. Paper towel dispenser mounted over grab bar | Employee Only Toilet Room - Meeting Hall | 1 | N/A | Priority 1 | Program Access | Provide at least one lavatory with knee and toe clearance positioned for a forward approach. Lower soap and paper towel dispensers to 42" max. above the floor. Relocate paper towel dispenser so that it is not mounted above the rear grab bar. | 1 | 2198
32 | Town Hall | C. Single-User Toilet | O. Hook located > 48" high | Employee Only Toilet Room - Meeting Hall | 1 | N/A | Priority 3 | Additional Access | Locate hook no higher than 48" above the finished floor. | 1 | 150
33 | Town Hall | F. Dispensers | D. Dispenser acts as a protruding object | Men’s Toilet Room - Lobby at Main Entrance | 1 | N/A | Priority 3 | Additional Access | Relocate paper towel dispenser out of the circulation path. | 1 | 256
34 | Town Hall | N/A | N/A | Meeting Hall Entrance | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing color contrast strips on the stair treads to increase visibility. | 1 | 0
35 | Town Hall | N/A | N/A | Meeting Hall | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing an adjustable-height podium. | 1 | 0
36 | Town Hall | N/A | N/A | Entrance to South Stairwell | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing color contrast strips on the stair treads to increase visibility. Recommend providing handrails with a 1-1/4"to 1-1/2" circular cross section, and ensuring that the sloped bottom extension extends one tread depth minimum beyond last riser nosing in same direction as stair flight. | 1 | 0
37 | Town Hall | N/A | N/A | Lobby From Main Entrance to Meeting Hall | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing designation signage with raised characters and braille where no signage is present. | 1 | 0
38 | Town Hall | N/A | N/A | West Side of Building | Ext | N/A | Priority 4 | Enhanced Usability | Recommend providing color contrast strips on the stair treads to increase visibility. Recommend providing handrails with a 1-1/4"to 1-1/2" circular cross section, and ensuring that the sloped bottom extension extends one tread depth minimum beyond last riser nosing in same direction as stair flight. Recommend providing a second handrail. | 1 | 0
39 | Town Hall | N/A | N/A | West Side of Building | Ext | N/A | Priority 4 | Enhanced Usability | Recommend repairing uneven surface at the top of the stairs to prevent tripping, although it is not part of the accessible route. | 1 | 0
40 | Town Hall | N/A | N/A | Accessible Entrance to Meeting Hall | Ext | N/A | Priority 4 | Enhanced Usability | Provide clear information about the locations of destination spaces at each entrance. Avoid terms such as "handicapped" and use the term "accessible" instead. | 1 | 0
1 | Transfer Station | A. Exterior Access Route | A. Not provided from all site arrival points | Battery Disposal Drop-Off | Exterior | N/A | Priority 1 | Program Access | Have staff provide assistance accessing the battery drop-off receptacles as needed. | 1 | 0
2 | Transfer Station | A. Exterior Access Route | A. Not provided from all site arrival points | Tires/CRT Monitors | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided from all points of arrival. Have staff provide assistance accessing the Tire/CRT drop-off receptacles as needed. | 1 | 0
3 | Transfer Station | A. Exterior Access Route | A. Not provided from all site arrival points | Service Window at Office | Exterior | N/A | Priority 1 | Program Access | Relocate mailbox so it does not block 36" min. wide accessible route to service counter. | 1 | 0
4 | Transfer Station | A. Exterior Access Route | A. Not provided from all site arrival points | Path to Service Window at Office | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided from all points of arrival. (Cost based on a straight pressure treated wood ramp that provides access to the door and the walkway leading to the service window. Ensure ramp includes a 5'x5' level landing where it meets the door and walkway.) | 1 | 1176
5 | Transfer Station | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) H. Running slope > 1:20 (5%) J. Level changes > 1/4" | Paper/ Newspaper & Mixed Drop-off | Exterior | N/A | Priority 3 | Additional Access | Have staff provide assistance accessing the paper drop-off receptacles as needed. | 1 | 0
6 | Transfer Station | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) H. Running slope > 1:20 (5%) J. Level changes > 1/4" | Glass Recycling Drop-off | Exterior | N/A | Priority 3 | Additional Access | Have staff provide assistance accessing the glass drop-off receptacles as needed. | 1 | 0
7 | Transfer Station | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) H. Running slope > 1:20 (5%) J. Level changes > 1/4" | Plastics 3 to 6 & No Number Drop-Off | Exterior | N/A | Priority 3 | Additional Access | Have staff provide assistance accessing the plastics drop-off receptacles as needed. | 1 | 0
8 | Transfer Station | A. Exterior Access Route | H. Running slope > 1:20 (5%) J. Level changes > 1/4" | Plastics 1 & 2 Only Drop-Off | Exterior | N/A | Priority 3 | Additional Access | Have staff provide assistance accessing the plastics drop-off receptacles as needed. | 1 | 0
9 | Transfer Station | A. Exterior Access Route | H. Running slope > 1:20 (5%) J. Level changes > 1/4" | Metal Drop-off | Exterior | N/A | Priority 3 | Additional Access | Have staff provide assistance accessing the metal drop-off receptacles as needed. | 1 | 0
10 | Transfer Station | A. Exterior Access Route | J. Level changes > 1/4" | Compactor/ Yellow Bag Household Trash | Exterior | N/A | Priority 3 | Additional Access | Have staff provide assistance accessing the yellow bag household waste drop-off receptacles as needed. | 1 | 0
11 | Transfer Station | A. Exterior Access Route | J. Level changes > 1/4" | Compactor 2 | Exterior | N/A | Priority 3 | Additional Access | Have staff provide assistance accessing compactor 2 as needed. | 1 | 0
12 | Transfer Station | B. Doors, Doorways, & Gates | G. Maneuvering clearance at door > 1:50 (2.00%) (MAAB) | Book Shed | Exterior | N/A | Priority 3 | Additional Access | Alter so that the slope in all directions is no greater than 1:50 (2.00%) yielding a 5'x5' level landing at the door. Cost to be determined based on specific remedy selected. | 1 | 0
13 | Transfer Station | B. Doors, Doorways, & Gates | G. Maneuvering clearance at door > 1:50 (2.00%) (MAAB) | Put-N-Take | Exterior | N/A | Priority 3 | Additional Access | Alter so that the slope in all directions is no greater than 1:50 (2.00%) yielding a 5'x5' level landing at the door. Cost to be determined based on specific remedy selected. | 1 | 0
14 | Transfer Station | F. Service Counter | B. Counter > 36" high | Service Window - Personal Shelter/ Office | Exterior | N/A | Priority 3 | Additional Access | Provide a counter that is 36" max. above the ground. | 1 | 880
15 | Transfer Station | G. Operable Parts | A. Element not on an accessible route | Used Oil Drop-Off | Exterior | N/A | Priority 1 | Program Access | Have staff provide assistance accessing the used oil drop-off receptacle as needed. | 1 | 0
16 | Transfer Station | G. Operable Parts | A. Element not on an accessible route | Cardboard Compactor | Exterior | N/A | Priority 1 | Program Access | Have staff provide assistance accessing the cardboard drop-off receptacles as needed. | 1 | 0
17 | Transfer Station | Q. Trash / Recycling | C. Trash container opening not within reach range | Book and Clothing Drop-off | Exterior | N/A | Priority 3 | Additional Access | Have staff provide assistance accessing the book and clothing recycling receptacles as needed. | 1 | 0
18 | Transfer Station | J. Portable Toilet | A. Not located on an accessible route B. Accessible portable toilets not provided | Portable Toilet | Exterior | N/A | Priority 1 | Program Access | Locate portable toilet on an accessible route. Ensure that at least 5% of portable toilets are accessible. | 1 | 4600
19 | Transfer Station | Buzzer or Intercom | N/A | Service Window - Personal Shelter/ Office | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a buzzer or intercom on an accessible route at base of recommended ramp proving an accessible route to the service window so visitors can notify staff that they may require assistance. Ensure the controls no higher than 48" above the ground. | 1 | 0

## Schools
Town of Sudbury: Priority for ADA Transition Plan - Schools | Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Column11 | Column12 | Column13 | Column14
| Priorities: Priority 1: Program Access* or Safety Priority 2: Navigational Issue Priority 3: Additional Access* Priority 4: Enhanced Usability | *Note: Some toilet rooms issues compromise Program Access. Some toilet rooms with less central issues (e.g., partially accessible toilet rooms), fall under Additional Access. | **IHCD Cost Estimation Notes: - Cost of design is not included. - Does not include costs when note indicates future work. - Labor cannot be estimated for all remedies. - There is no cost noted when it's presumed to be a maintenance issue. - Cost based on a national average. Cost is not based on prevailing wage. - There is no cost noted when it's presumed to be a maintenance issue. Estimates are intended as a guide to budgeting access modifications and are not intended to be absolutely comprehensive or definitive.
| Information Provided by Institute for Human Centered Design | [10 empty] | Project Management for the Town of Sudbury
ID | Facility Name | Element | Issue/Physical Barrier | Location | Floor | Room | Town Priority | Priority for Barrier Removal | Remedies | Quantity | Estimated Cost of Barrier Removal | Project Start Date | Project Completion Date | Responsible for Barrier Removal
1 | Curtis Middle School | A. Exterior Access Route | H. Running slope > 1:20 (5%) | Parking 1 Lower Level A Opposite Main Entrance | Exterior | N/A | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:20 (5%). (Cost based on adding asphalt to reduce slope at base of walkway.) | 1 | 480
2 | Curtis Middle School | A. Exterior Access Route | H. Running slope > 1:20 (5%) | Parking 1 Lower Level B | Exterior | N/A | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:20 (5%). (Cost based on adding asphalt to reduce slope at base of walkway.) | 1 | 480
3 | Curtis Middle School | A. Exterior Access Route | H. Running slope > 1:20 (5%) | Egress Door 13 | Exterior | N/A | Priority 3 | Additional Access | Reduce running slope to be no steeper than 1:20 (5%). (Cost for adding concrete to correct pathway running slope.) | 1 | 240
4 | Curtis Middle School | A. Exterior Access Route | H. Running slope > 1:20 (5%) | Egress Door 10 | Exterior | N/A | Priority 3 | Additional Access | Reduce running slope to 1;50 (2.00%) max. at door landing. (Cost for adding asphalt to correct pathway running slope.) | 1 | 240
5 | Curtis Middle School | A. Exterior Access Route | M. Route not maintained in operable working condition | Parking 1 Opposite Main Entrance | Exterior | N/A | Priority 1 | Program Access | Ensure the accessible route is maintained in operable working condition. | 1 | 0
6 | Curtis Middle School | A. Exterior Access Route | M. Route not maintained in operable working condition | Path Leading to Sitting Area at the Softball Field | Exterior | N/A | Priority 1 | Program Access | Ensure the accessible route is maintained in operable working condition. | 1 | 0
7 | Curtis Middle School | A. Exterior Access Route | N. Accessible route not provided | Main Entrance- Fire Box | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided. (Cost based on a 4' wide min. x 6' concrete route to fire box.) | 1 | 384
8 | Curtis Middle School | A. Exterior Access Route | N. Accessible route not provided | Bike Racks | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided. Reduce running slope at bike rack to 1:50 (2.00%) in all directions. (Cost based on adding concrete at bike rack to reduce slope.) | 1 | 240
9 | Curtis Middle School | C. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces C. Total # of designated van accessible spaces O. Sign does not have the designation "Van Accessible" P. Sign bottom < 60" above finished grade | Parking 1 Lower Level A Opposite Main Entrance | Exterior | N/A | Priority 1 | Program Access | Add the designation "Van Accessible" to the sign located at the van accessible space. Locate sign with the bottom of the sign 60" above the ground. above the ground. | 1 | 500
10 | Curtis Middle School | C. Off-Street Parking Lot or Garage | B. Total # of designated accessible parking spaces C. Total # of designated van accessible spaces O. Sign does not have the designation "Van Accessible" P. Sign bottom < 60" above finished grade | Parking 1 Lower Level B | Exterior | N/A | Priority 1 | Program Access | Add the designation "Van Accessible" to the sign located at the van accessible space. Locate sign with the bottom of the sign 60" above the ground. | 1 | 500
11 | Curtis Middle School | H. Emergency Exit | A. Tactile sign not provided at emergency exit B. Tactile sign not provided at exit | Egress Door 9 | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. | 1 | 232
12 | Curtis Middle School | H. Emergency Exit | B. Tactile sign not provided at exit | Egress Door 5 | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. | 1 | 232
13 | Curtis Middle School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Main Entrance - Egress Door 1 | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
14 | Curtis Middle School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Egress Door 4 | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
15 | Curtis Middle School | A. Means of Egress | B. Tactile exit sign not provided | Egress Door 3 | 1 | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. | 1 | 232
16 | Curtis Middle School | A. Means of Egress | B. Tactile exit sign not provided | Music Lab/ Electronic Room | 1 | 175 | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. | 1 | 232
17 | Curtis Middle School | A. Means of Egress | B. Tactile exit sign not provided O. Illuminated ISA symbol not provided (MAAB) | Egress Door 15 | 1 | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
18 | Curtis Middle School | A. Means of Egress | B. Tactile exit sign not provided O. Illuminated ISA symbol not provided (MAAB) | Auditorium Egress Door 14 | 1 | 1320 | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
19 | Curtis Middle School | A. Means of Egress | B. Tactile exit sign not provided O. Illuminated ISA symbol not provided (MAAB) | Egress Door 8 | 1 | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
20 | Curtis Middle School | A. Means of Egress | B. Tactile exit sign not provided O. Illuminated ISA symbol not provided (MAAB) | Egress Door 11 | 1 | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility | 1 | 432
21 | Curtis Middle School | A. Means of Egress | B. Tactile exit sign not provided O. Illuminated ISA symbol not provided (MAAB) | Egress Door 10 | 1 | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
22 | Curtis Middle School | B. Interior Access Route | A. Route < 36" wide | Technology Center | 2 | N/A | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. | 1 | 0
23 | Curtis Middle School | B. Interior Access Route | A. Route < 36" wide | Corridor Leading to More Counselor's Offices | 2 | N/A | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. | 1 | 0
24 | Curtis Middle School | B. Interior Access Route | B. Obstructed by protruding objects | Auditorium | 1 | 1320 | Priority 3 | Additional Access | Relocate defibrillator or provide a cane-detectable barrier. | 1 | 306
25 | Curtis Middle School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Single-User Toilet Room | 1 | N/A | Priority 3 | Additional Access | Remove the table to provide 18" min. pull-side maneuvering clearance at door. | 1 | 0
26 | Curtis Middle School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Men’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Provide an automatic door opener. | 1 | 3060
27 | Curtis Middle School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Principal's Office | 1 | N/A | Priority 3 | Additional Access | Remove the mailbox to provide 18" min. pull-side maneuvering clearance at door. | 1 | 0
28 | Curtis Middle School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Stair 2 | 2 | N/A | Priority 3 | Additional Access | Remove stored items to provide 18" min. pull side maneuvering clearance at door. | 1 | 0
29 | Curtis Middle School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Grade 7 Technology Engineering | 2 | 260 | Priority 3 | Additional Access | Remove the desk to provide maneuvering clearance. | 1 | 0
30 | Curtis Middle School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Grade 6 Guidance Councilor | 2 |  | Priority 3 | Additional Access | Remove shelves to provide 18" min. pull-side maneuvering clearance at door. | 1 | 0
31 | Curtis Middle School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Grade 7 SS | 2 | 215 | Priority 3 | Additional Access | Remove trash can to provide 12" min. push-side maneuvering clearance at door. | 1 | 0
32 | Curtis Middle School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Music Band | 1 | 184 | Priority 3 | Additional Access | Remove file cabinet to provide 18" min. pull-side maneuvering clearance. | 1 | 0
33 | Curtis Middle School | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Reception | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. Note: Adding an additional handle to the horizontal metal portion of the door above the existing hardware could result in a door opening solution that could be used without requiring tight grasping, pinching or twisting of the wrist.) | 1 | 484
34 | Curtis Middle School | C. Doors, Doorways, & Gates | M. Door requires > 5 lbs. of force to open | Principal | 1 | N/A | Priority 3 | Additional Access | Adjust closers so doors do not require more than 5 pounds of force to open. | 1 | 0
35 | Curtis Middle School | C. Doors, Doorways, & Gates | M. Door requires > 5 lbs. of force to open | Reception | 1 | N/A | Priority 3 | Additional Access | Adjust closers so doors do not require more than 5 pounds of force to open. | 1 | 0
36 | Curtis Middle School | G. Elevator | L. Tactile stars not provided at main entry level | Elevator | 1 | N/A | Priority 3 | Additional Access | Provide a tactile star on both sides of jambs at main floor. At other floors, provide appropriate number. Provide a tactile star at the main floor on the control panel within the car. | 2 | 192
37 | Curtis Middle School | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Cafeteria | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
38 | Curtis Middle School | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Auditorium/ Gymnasium Doorway | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
39 | Curtis Middle School | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Technology Center | 2 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. (Ensure signs are up-to-date and that accurate raised characters and braille are provided.) | 1 | 232
40 | Curtis Middle School | H. Signage | D. Braille not provided on sign | Kitchen | 1 | N/A | Priority 2 | Navigational Issue | Provide braille on sign. | 1 | 232
41 | Curtis Middle School | H. Signage | D. Braille not provided on sign | Men’s Toilet Room | 1 | N/A | Priority 2 | Navigational Issue | Provide braille on sign. | 1 | 232
42 | Curtis Middle School | H. Signage | G. Sign not located on the latch side of the door | Custodian | 1 | N/A | Priority 2 | Navigational Issue | Locate sign at permanent rooms alongside the door on the latch side. | 1 | 0
43 | Curtis Middle School | H. Signage | G. Sign not located on the latch side of the door | Grade 8 Bridges Program | 1 | 106 | Priority 2 | Navigational Issue | Locate sign at permanent rooms alongside the door on the latch side. | 1 | 0
44 | Curtis Middle School | H. Signage | G. Sign not located on the latch side of the door | Grade 8 Green SS | 1 | 115 | Priority 2 | Navigational Issue | Locate sign at permanent rooms alongside the door on the latch side. | 1 | 0
45 | Curtis Middle School | H. Signage | G. Sign not located on the latch side of the door | Grade 7 SpED LEAP | 2 | 206 | Priority 2 | Navigational Issue | Locate sign at permanent rooms alongside the door on the latch side. | 1 | 0
46 | Curtis Middle School | K. Operable Parts | H. Not operable with a closed fist | Main Entrance - Library Book Return | Exterior | N/A | Priority 3 | Additional Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 200
47 | Curtis Middle School | M. Dining or Work Surfaces | B. At least one or 5% accessible tables not provided | Cafeteria | 1 | N/A | Priority 1 | Program Access | Ensure that at least 5% of dining or work surfaces are accessible.(Cost based on three accessible dining surfaces.) | 3 | 3300
48 | Curtis Middle School | M. Dining or Work Surfaces | B. At least one or 5% accessible tables not provided | Grade 8 Special Ed Skills | 1 | 147 | Priority 1 | Program Access | Ensure that at least one work surface is accessible. | 1 | 700
49 | Curtis Middle School | M. Dining or Work Surfaces | B. At least one or 5% accessible tables not provided | Grade 6 SS Class | 3 | 309 | Priority 1 | Program Access | Ensure that at least one work surface is accessible. | 1 | 700
50 | Curtis Middle School | M. Dining or Work Surfaces | B. At least one or 5% accessible tables not provided | Grade 6 Science Class | 3 | 306 | Priority 1 | Program Access | Ensure that at least one work surface is accessible. | 1 | 700
51 | Curtis Middle School | M. Dining or Work Surfaces | B. At least one or 5% accessible tables not provided | Grade 6 ELA Class | 3 | 318 | Priority 1 | Program Access | Ensure that at least one work surface is accessible. | 1 | 700
52 | Curtis Middle School | M. Dining or Work Surfaces | B. At least one or 5% accessible tables not provided | Computer Lab | 2 | 269 | Priority 1 | Program Access | Ensure that at least one work surface is accessible. | 1 | 700
53 | Curtis Middle School | M. Dining or Work Surfaces | B. At least one or 5% accessible tables not provided | Grade 7 SpED LEAP | 2 | 206 | Priority 1 | Program Access | Ensure that at least one work surface is accessible. | 1 | 700
54 | Curtis Middle School | M. Dining or Work Surfaces | B. At least one or 5% accessible tables not provided | Grade 7 ELA | 2 | 212 | Priority 1 | Program Access | Ensure that at least one work surface is accessible. | 1 | 700
55 | Curtis Middle School | M. Dining or Work Surfaces | B. At least one or 5% accessible tables not provided | Grade 7 SS | 2 | 215 | Priority 1 | Program Access | Ensure that at least one work surface is accessible. | 1 | 700
56 | Curtis Middle School | M. Dining or Work Surfaces | B. At least one or 5% accessible tables not provided | Learning Center | 2 | 221 | Priority 1 | Program Access | Ensure that at least one work surface is accessible. | 1 | 700
57 | Curtis Middle School | M. Dining or Work Surfaces | B. At least one or 5% accessible tables not provided | Music Lab/ Electronic Room | 1 | 175 | Priority 1 | Program Access | Ensure that at least one work surface is accessible. | 1 | 700
58 | Curtis Middle School | N. Assembly Area | P. Assistive listening devices not provided | Auditorium | 1 | 1320 | Priority 1 | Program Access | If audible communication is integral to the use of the space, provide an assistive listening system. | 1 | 1214
59 | Curtis Middle School | N. Assembly Area | P. Assistive listening devices not provided | Library | 2 | N/A | Priority 1 | Program Access | If audible communication is integral to the use of the space, provide an assistive listening system. | 1 | 1214
60 | Curtis Middle School | O. Locker Room | J. 5% of changing rooms are not accessible | Women’s Locker Room | 1 | N/A | Priority 1 | Program Access | Provide an accessible changing room. | 1 | 5866
61 | Curtis Middle School | O. Locker Room | O. Back support not provided at bench | Men’s Locker Room | 1 | N/A | Priority 3 | Additional Access | Provide at least one bench with back support or that is affixed to a wall with room on the side to transfer. | 1 | 200
62 | Curtis Middle School | O. Locker Room | O. Back support not provided at bench | Women’s Locker Room | 1 | N/A | Priority 3 | Additional Access | Provide at least one bench with back support or that is affixed to a wall with room on the side to transfer. | 1 | 200
63 | Curtis Middle School | P. Laboratory | B. At least one (or 5%) acc. work surface not provided | Science Prep | 1 | N/A | Priority 1 | Program Access | Alter so that 5% of work surfaces (at least one) are 28"- 34" above the floor with knee and toe clearance positioned for a forward approach. | 1 | 880
64 | Curtis Middle School | P. Laboratory | E. Emergency shower out of reach range | Science Room | 1 | N/A | Priority 3 | Additional Access | Lower the shower pull to 48" max. above the floor. | 1 | 0
65 | Curtis Middle School | P. Laboratory | E. Emergency shower out of reach range | Science Room | 1 | N/A | Priority 3 | Additional Access | Lower the shower pull to 48" max. above the floor. | 1 | 0
66 | Curtis Middle School | P. Laboratory | E. Emergency shower out of reach range | Grade 8 Green Science | 1 | 127 | Priority 3 | Additional Access | Lower the shower pull to 48" max. above the floor. | 1 | 0
67 | Curtis Middle School | S. Picnic Tables | C. At least 5% accessible spaces not provided H. Picnic table not on an accessible route | Main Entrance | Exterior | N/A | Priority 1 | Program Access | Ensure that at least 5% (minimum one) of picnic tables are accessible. Ensure that the accessible picnic table is connected to an accessible route. | 1 | 1400
68 | Curtis Middle School | T. Exterior Benches | A. No accessible route to one bench in area | Bench at Bike Rack | Exterior | N/A | Priority 1 | Program Access | Relocate bench to an accessible route. | 1 | 0
69 | Curtis Middle School | B. Lavatory | A. Clear floor space not provided at lavatory | Women’s Toilet Room Near Cafeteria and Locker Rooms | 1 | N/A | Priority 3 | Additional Access | Provide at least one lavatory with a 30" min. by 48" min. clear floor space positioned for a forward approach. (Relocate the paper towel dispenser out of the clear floor space in front of the lavatory that is made accessible.) | 1 | 353
70r | Curtis Middle School | B. Lavatory | A. Clear floor space not provided at lavatory | Men’s Toilet Room Near Cafeteria and Locker Rooms | 1 | N/A | Priority 3 | Additional Access | Provide at least one lavatory with a 30" min. by 48" min. clear floor space positioned for a forward approach. (Relocate the paper towel dispenser out of the clear floor space in front of the lavatory that is made accessible.) | 1 | 353
71 | Curtis Middle School | B. Lavatory | E. Plumbing underneath is exposed | Men’s Toilet Room | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact for at least one lavatory. | 1 | 92
72 | Curtis Middle School | B. Lavatory | E. Plumbing underneath is exposed | Men’s Locker Room | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact for at least one lavatory. | 1 | 92
73 | Curtis Middle School | B. Lavatory | E. Plumbing underneath is exposed | Women’s Locker Room | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact for at least one lavatory. | 1 | 92
74 | Curtis Middle School | B. Lavatory | E. Plumbing underneath is exposed | Women’s Toilet Room Section A | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact for at least one lavatory. | 1 | 92
75 | Curtis Middle School | C. Single-User Toilet | B. Flush control not on open side | Lavatory - Health Office | 1 | N/A | Priority 3 | Additional Access | Relocate the flush control to the open side. | 1 | 374
76 | Curtis Middle School | C. Single-User Toilet | B. Flush control not on open side | Single-User Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate the flush control to the open side. | 1 | 374
77 | Curtis Middle School | C. Single-User Toilet | B. Flush control not on open side | Toilet Room 2 Section A | 1 | N/A | Priority 3 | Additional Access | Relocate the flush control to the open side. | 1 | 374
78 | Curtis Middle School | C. Single-User Toilet | Non-compliant paper towel dispenser. | Single-User Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate dispenser from above grab bar. | 1 | 353
79 | Curtis Middle School | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Men’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
80 | Curtis Middle School | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Men’s Locker Room Accessible Compartment | 1 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
81 | Curtis Middle School | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Women’s Toilet Room Near Cafeteria and Locker Rooms | 1 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
82 | Curtis Middle School | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Men’s Toilet Room Near Cafeteria and Locker Rooms | 1 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
83 | Curtis Middle School | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Women’s Toilet Room Section A | 1 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
84 | Curtis Middle School | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Men’s Toilet Room | 3 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
85 | Curtis Middle School | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Women’s Toilet Room | 3 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
86 | Curtis Middle School | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Women's Toilet Room | 2 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
87 | Curtis Middle School | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Men’s Toilet Room | 2 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
88 | Curtis Middle School | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Men's Toilet Room | 2 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
89 | Curtis Middle School | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Women’s Toilet Room | 2 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
90 | Curtis Middle School | D. Toilet Compartment | M. Flush control not on open side | Women’s Locker Room | 1 | N/A | Priority 3 | Additional Access | Provide the flush control on the open side of the toilet (transfer side). | 1 | 374
91 | Curtis Middle School | D. Toilet Compartment | M. Flush control not on open side | Women’s Toilet Room Near Cafeteria and Locker Rooms | 1 | N/A | Priority 3 | Additional Access | Provide the flush control on the open side of the toilet (transfer side). | 1 | 374
92 | Curtis Middle School | D. Toilet Compartment | M. Flush control not on open side | Women's Toilet Room | 2 | N/A | Priority 3 | Additional Access | Provide the flush control on the open side of the toilet (transfer side). | 1 | 374
93 | Curtis Middle School | D. Toilet Compartment | N. Non-compliant toilet paper dispenser | Women’s Toilet Room | 3 | N/A | Priority 3 | Additional Access | Relocate toilet paper so that it is 24" min. high, located under the grab bar, and between 7" and 9" from the front of the toilet./Replace dispenser as it does not allow continuous paper flow. | 1 | 353
94 | Curtis Middle School | E. Urinal | D. Urinal recessed > 24" has > 36" clear width | Men’s Toilet Room | 1 | N/A | Priority 1 | Program Access | If urinal is recessed greater than 24" ensure there is a clear width of 36". | 1 | 353
95 | Curtis Middle School | E. Urinal | D. Urinal recessed > 24" has > 36" clear width | Men’s Toilet Room | 3 | N/A | Priority 1 | Program Access | If urinal is recessed greater than 24" ensure there is a clear width of 36". | 1 | 353
96 | Curtis Middle School | E. Urinal | D. Urinal recessed > 24" has > 36" clear width | Men's Toilet Room | 2 | N/A | Priority 1 | Program Access | If urinal is recessed greater than 24" ensure there is a clear width of 36". | 1 | 353
97 | Curtis Middle School | F. Dispensers | A. Controls > 42" high | Grade 7 Technology Engineering | 2 | 260 | Priority 3 | Additional Access | If it is used by students, relocate paper towel dispenser so the operable part is 42" max. above the finished floor. | 1 | 256
98 | Curtis Middle School | F. Dispensers | D. Dispenser acts as a protruding object | Single-User Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate dispenser out of the circulation path or provide a cane-detectible barrier under the dispenser. | 1 | 306
99 | Curtis Middle School | F. Dispensers | D. Dispenser acts as a protruding object | Single-User Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate dispenser out of the circulation path or provide a cane-detectible barrier under the dispenser. | 1 | 306
100 | Curtis Middle School | F. Dispensers | D. Dispenser acts as a protruding object | Women’s Toilet Room Near Cafeteria and Locker Rooms | 1 | N/A | Priority 3 | Additional Access | Relocate dispenser out of the circulation path or provide a cane-detectible barrier. | 1 | 306
101 | Curtis Middle School | F. Dispensers | D. Dispenser acts as a protruding object | Men’s Toilet Room Near Cafeteria and Locker Rooms | 1 | N/A | Priority 3 | Additional Access | Relocate dispenser out of the circulation path or provide a cane-detectible barrier. | 1 | 306
102 | Curtis Middle School | F. Dispensers | D. Dispenser acts as a protruding object | Men’s Toilet Room | 3 | N/A | Priority 3 | Additional Access | Relocate dispenser out of the circulation path or provide a cane-detectible barrier. | 1 | 306
103 | Curtis Middle School | F. Dispensers | D. Dispenser acts as a protruding object | Women's Toilet Room | 2 | N/A | Priority 3 | Additional Access | Relocate paper towel dispenser out of the circulation path or provide a cane-detectible barrier. | 1 | 306
104 | Curtis Middle School | F. Dispensers | D. Dispenser acts as a protruding object | Men’s Toilet Room | 2 | N/A | Priority 3 | Additional Access | Relocate paper towel dispenser out of the circulation path or provide a cane-detectible barrier. | 1 | 306
105 | Curtis Middle School | F. Dispensers | D. Dispenser acts as a protruding object | Men's Toilet Room | 2 | N/A | Priority 3 | Additional Access | Relocate paper towel dispenser out of the circulation path or provide a cane-detectible barrier. | 1 | 306
106 | Curtis Middle School | F. Dispensers | D. Dispenser acts as a protruding object | Men’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate dispenser out of the circulation path or provide a cane-detectible barrier under the dispenser. | 1 | 306
107 | Curtis Middle School | G. Shower Compartment | E. Grab bars not provided | Women’s Locker Room | 1 | N/A | Priority 1 | Program Access | Provide compliant grab bars. For a roll-in shower with a seat, grab bars shall be provided on the back wall and side wall opposite the seat. | 1 | 898
108 | Curtis Middle School | G. Shower Compartment | E. Grab bars not provided G. Grab bars mounted in wrong location | Men’s Locker Room | 1 | N/A | Priority 1 | Program Access | Provide grab bar on back wall. Ensure grab bars are not provided over the seat. For a roll-in shower with a seat, grab bars shall be provided on the back wall and side wall opposite the seat. | 1 | 1154
109 | Curtis Middle School | A. Drinking Fountains | H. No drinking fountain provided for standing users L. Knee or toe clearance not provided | Drinking Fountain Next to 301 | 3 | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users or install a Hi-Lo drinking fountain. Provide knee and toe clearance, 27" min. high at drinking fountain for seated users. (Cost based on a new Hi-Lo fountain.) | 1 | 4216
110 | Curtis Middle School | B. Sink | B. Toe and knee clearances not provided | Science Prep | 1 | N/A | Priority 1 | Program Access | If the sinks in this area are used by students, ensure there is a 27" knee clearance positioned for a forward approach at at least one sink in the lab. | 1 | 1686
111 | Curtis Middle School | B. Sink | B. Toe and knee clearances not provided | Grade 7 Technology Engineering | 2 | 260 | Priority 1 | Program Access | If the sink in this area is used by students, ensure there is a 27" knee clearance positioned for a forward approach. | 1 | 1686
112 | Curtis Middle School | C. Field | A. Accessible spaces not provided at team seating | Baseball Team Seating 1 | Exterior | N/A | Priority 1 | Program Access | Provide a firm, stable and slip resistant path and surface 48" wide min. to the baseball field team seating and at a 36" x 48" clear floor space by the team seating. (Cost based on an asphalt path and patch by the bench positioned to allow shoulder alignment with a person seated at the bench for someone using a wheeled mobility device.) | 1 | 360
113 | Curtis Middle School | C. Field | A. Accessible spaces not provided at team seating | Baseball Team Seating 2 | Exterior | N/A | Priority 1 | Program Access | Provide a firm, stable and slip resistant path and surface 48" wide min. to the baseball field team seating and at a 36" x 48" clear floor space by the team seating. (Cost based on an asphalt path and patch by the bench positioned to allow shoulder alignment with a person seated at the bench for someone using a wheeled mobility device.) | 1 | 360
114 | Curtis Middle School | C. Field | A. Accessible spaces not provided at team seating | Team Seating 1 at Softball Field | Exterior | N/A | Priority 1 | Program Access | Provide a firm, stable and slip resistant path and surface 48" wide min. to the softball field team seating and at a 36" x 48" clear floor space by the team seating. (Cost based on an asphalt path and patch by the bench positioned to allow shoulder alignment with a person seated at the bench for someone using a wheeled mobility device.) | 1 | 360
115 | Curtis Middle School | C. Field | A. Accessible spaces not provided at team seating | Team Seating 2 at Softball Field | Exterior | N/A | Priority 1 | Program Access | Provide a firm, stable and slip resistant path and surface 48" wide min. to the softball field team seating and at a 36" x 48" clear floor space by the team seating. (Cost based on an asphalt path and patch by the bench positioned to allow shoulder alignment with a person seated at the bench for someone using a wheeled mobility device.) | 1 | 360
116 | Curtis Middle School | C. Field | C. Field not connected to an accessible route | Softball Field Entrance by Team Seating 2 | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the edge of sport activity at the softball field. Provide a firm, stable and slip resistant surface 48" wide min. with a max. running slope of 1:20 (5.00%) and a max. cross slope of 1:50 (2.00%). | 1 | 480
117 | Curtis Middle School | C. Field | C. Field not connected to an accessible route | Softball Field Entrance by Team Seating 2 | Exterior | N/A | Priority 1 | Program Access | Reduce change in level to 1/2" max. | 1 | 0
118 | Curtis Middle School | C. Field | A. Accessible spaces not provided at team seating | Team Seating at the Soccer Field | Exterior | N/A | Priority 1 | Program Access | Provide a firm, stable and slip resistant path and surface 48" wide min. to the soccer field team seating and at a 36" x 48" clear floor space by the team seating. (Cost based on an asphalt path and patch by the bench positioned to allow shoulder alignment with a person seated at the bench for someone using a wheeled mobility device.) | 1 | 360
119 | Curtis Middle School | C. Field | C. Field not connected to an accessible route | Open Field Entrance | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the edge of sport activity at the soccer field. Provide a firm, stable and slip resistant surface 48" wide min. with a max. running slope of 1:20 (5.00%) and a max. cross slope of 1:50 (2.00%). | 1 | 480
120 | Curtis Middle School | D. Court | C. Court is not connected to an accessible route | Basketball Court | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the edge of sport activity at the basketball court. Provide a firm, stable and slip resistant surface 48" wide min. with a max. running slope of 1:20 (5.00%) and a max. cross slope of 1:50 (2.00%). | 1 | 480
121 | Curtis Middle School | Egress Walkway | N/A | Egress Door 9 | 1 | N/A | Priority 4 | Enhanced Usability | Recommend extending walkway from egress door to paved surface. | 1 | 0
122 | Curtis Middle School | Egress Walkway | N/A | Egress Door 6 - 9 | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend extending walkway from egress door to paved surface. | 1 | 0
123 | Curtis Middle School | Podium | N/A | Auditorium | 1 | 1320 | Priority 4 | Enhanced Usability | Recommend providing an adjustable height podium with knee and toe clearance. | 1 | 0
1 | Haynes Elementary School | A. Exterior Access Route | F. Surface openings > 1/2" J. Level changes > 1/4" | Exit From Corridor by Rooms 22 and 23 | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. and ensure that surface openings are no greater than 1/2". (Cost estimate for asphalt.) | 1 | 320
2 | Haynes Elementary School | A. Exterior Access Route | F. Surface openings > 1/2" K. Surface is not stable, firm, and slip-resistant | Walkway by Exit Door 3 | Exterior | N/A | Priority 3 | Additional Access | Repair gaps in surface. | 1 | 160
3 | Haynes Elementary School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Rear Southwest Parking Lot Accessible Parking Space | Exterior | N/A | Priority 1 | Program Access | Reduce cross slope to be no steeper than 1:50 (2.00%). (Cost for 10' long by 5' wide asphalt area.) | 1 | 500
4 | Haynes Elementary School | A. Exterior Access Route | J. Level changes > 1/4" | Walkway by Exit Door 6 | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. | 1 | 160
5 | Haynes Elementary School | A. Exterior Access Route | J. Level changes > 1/4" | Sidewalk by Exit Door 9 to Accessible Parking Space in Rear Lot | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. (Cost estimate for asphalt.) | 1 | 160
6 | Haynes Elementary School | A. Exterior Access Route | K. Surface is not stable, firm, and slip-resistant | Area by Exit Door 11 | Ext | 9 | Priority 3 | Additional Access | Repair surface. | 1 | 160
7 | Haynes Elementary School | A. Exterior Access Route | K. Surface is not stable, firm, and slip-resistant | Walkway by Exit From Corridor by Rooms 22 and 23 | Exterior | N/A | Priority 3 | Additional Access | Repair surface at gate. | 1 | 160
8 | Haynes Elementary School | A. Exterior Access Route | K. Surface is not stable, firm, and slip-resistant | Exit Door 10 From Partners Program (Grades 3-5) | Exterior | 8 | Priority 3 | Additional Access | Repair surface at transition between concrete and asphalt. | 1 | 160
9 | Haynes Elementary School | A. Exterior Access Route | N. Accessible route not provided | Bike Rack by Exit Door 3 | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided to the bike rack. (Cost estimate for a 6' long 4' wide asphalt route.) | 1 | 240
10 | Haynes Elementary School | A. Exterior Access Route | N. Accessible route not provided | Picnic Table and Bench Area | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to one picnic table and one bench in this area. (Cost estimate for 20' long 4' wide asphalt route.) | 1 | 800
11 | Haynes Elementary School | B. Curb Ramp | A. Curb ramp not provided | East Crosswalk | Exterior | N/A | Priority 1 | Program Access | Provide a curb ramp at this intersection and at the end of the walkway on the east. (Cost estimate for a concrete curb ramp.) | 2 | 5600
12 | Haynes Elementary School | B. Curb Ramp | J. Landing not provided at top of curb ramp | Northeast Parking Lot | Exterior | N/A | Priority 1 | Program Access | Provide landing at top of curb ramp or reconfigure ramp. (Cost estimate for new concrete curb ramp.) | 1 | 2800
13 | Haynes Elementary School | B. Curb Ramp | N. Surface not stable, firm and slip-resistant | East Crosswalk by Main Entrance | Exterior | N/A | Priority 1 | Program Access | Repair surface for gaps and changes in level. | 1 | 144
14 | Haynes Elementary School | B. Curb Ramp | N. Surface not stable, firm and slip-resistant | Curb Ramp by Exit Door 6 | Exterior | N/A | Priority 1 | Program Access | Repair surface for gaps and changes in level. | 1 | 144
15 | Haynes Elementary School | B. Curb Ramp | N. Surface not stable, firm and slip-resistant | Curb Ramp by Exit Door 9 | Exterior | N/A | Priority 1 | Program Access | Repair surface for gaps and changes in level. | 1 | 144
16 | Haynes Elementary School | C. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces C. Total # of designated van accessible spaces O. Sign does not have the designation "Van Accessible" P. Sign bottom < 60" above finished grade | Southeast Parking Lot | Exterior | N/A | Priority 1 | Program Access | Provide one additional car accessible parking space. Add the designation "Van Accessible" to the sign located at the van accessible space. Locate sign with the bottom of the sign 60" above the ground. | 1 | 2350
17 | Haynes Elementary School | C. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces C. Total # of designated van accessible spaces O. Sign does not have the designation "Van Accessible" | Rear Southwest Parking Lot Accessible Parking Space | Exterior | N/A | Priority 1 | Program Access | Add the designation "Van Accessible" to the sign located at the accessible space. | 1 | 500
18 | Haynes Elementary School | H. Emergency Exit | N/A | Exit Door 16 | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing accessible routes from all exit doors. | 1 | 0
19 | Haynes Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided | Learning Center for Grades 4-5 Exit Door 17 | 1 | 15 | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. | 1 | 464
20 | Haynes Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided | Exit Door 18 | 1 | 16 | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. | 1 | 464
21 | Haynes Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided | Exit Doors From Classrooms | 1 | 19 20 | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. | 2 | 928
22 | Haynes Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided | Exit Doors From Classrooms | 1 | 21 22 | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. | 2 | 928
23 | Haynes Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided G. Maneuvering clearance(s) not provided | Grade 4 Exit Door 16 | 1 | 13 | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. Relocate the table that is blocking the door. | 1 | 464
24 | Haynes Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Front Lobby | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
25 | Haynes Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Exit Door 6 by ESL | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
26 | Haynes Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Exit From Corridor by Rooms 22 and 23 | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
27 | Haynes Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Exit Door 15 by Art Classroom | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
28 | Haynes Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Exit Door 14 From Gym | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
29 | Haynes Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Exit Door 13 From Gym | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
30 | Haynes Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Exit Door 12 From Gym | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
31 | Haynes Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Exit Door 9 | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
32 | Haynes Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Exit Door 7 | 1 | 6 | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
33 | Haynes Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Exit Door 8 | 1 | 7 | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
34 | Haynes Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Partners Program (Grades 3-5) Egress Door 10 | 1 | 8 | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
35 | Haynes Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) G. Maneuvering clearance(s) not provided | Partners Program (Grades K-2) Exit Door 11 | 1 | 9 | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. Relocate furniture. | 1 | 432
36 | Haynes Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) L. Mat not securely attached | Exit Door 3 to the Parking Lot on the Side of the School | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. Secure the mat. | 1 | 432
37 | Haynes Elementary School | H. Emergency Exit | G. Maneuvering clearance(s) not provided | Partners Program (Grades 3-5) Egress Door 10 | 1 | 8 | Priority 3 | Additional Access | Relocate furniture that blocks access to the emergency exit. | 1 | 0
38 | Haynes Elementary School | B. Interior Access Route | A. Route < 36" wide | Library | 1 | N/A | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. Note: Route can narrow to 32" for 24" of depth. | 1 | 0
39 | Haynes Elementary School | B. Interior Access Route | A. Route < 36" wide | Library | 1 | N/A | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. Note: Route can narrow to 32" for 24" of depth. | 1 | 0
40 | Haynes Elementary School | B. Interior Access Route | A. Route < 36" wide | Library | 1 | N/A | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. Note: Route can narrow to 32" for 24" of depth. | 1 | 0
41 | Haynes Elementary School | B. Interior Access Route | A. Route < 36" wide | Speech Language & Counseling Waiting Area | 1 | N/A | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. Note: Route can narrow to 32" for 24" of depth. | 1 | 0
42 | Haynes Elementary School | B. Interior Access Route | A. Route < 36" wide | Speech Language & Counseling Waiting Area | 1 | N/A | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. Note: Route can narrow to 32" for 24" of depth. | 1 | 0
43 | Haynes Elementary School | B. Interior Access Route | A. Route < 36" wide | Partners Program (Grades 3-5) | 1 | 8 | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. Route is able to narrow to 32" for 24" min. deep. | 1 | 0
44 | Haynes Elementary School | B. Interior Access Route | A. Route < 36" wide B. Obstructed by protruding objects | Girls' Toilet Room Across From Auditorium | 1 | N/A | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. Relocate paper towel dispenser so that it does not obstruct the clear width and does not act as a protruding object. | 1 | 353
45 | Haynes Elementary School | B. Interior Access Route | B. Obstructed by protruding objects | Health Office Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate white storage box. It acts as a protruding object and projects into the clear space required at the toilet. | 1 | 353
46 | Haynes Elementary School | B. Interior Access Route | B. Obstructed by protruding objects | Lobby | 1 | N/A | Priority 3 | Additional Access | Provide a cane-detectable barrier along each side. | 2 | 612
47 | Haynes Elementary School | B. Interior Access Route | B. Obstructed by protruding objects | Auditorium/ Cafeteria | 1 | N/A | Priority 3 | Additional Access | Relocate paper towel dispenser and cleansing wipe dispenser out of the circulation path. | 2 | 512
48 | Haynes Elementary School | B. Interior Access Route | B. Obstructed by protruding objects | Grade 2 Grade 1 | 1 | 19 21 | Priority 3 | Additional Access | Relocate paper towel dispensers out of the circulation path. | 2 | 512
49 | Haynes Elementary School | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Library | 1 | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
50 | Haynes Elementary School | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Library | 1 | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
51 | Haynes Elementary School | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Library | 1 | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
52 | Haynes Elementary School | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Library | 1 | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
53 | Haynes Elementary School | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Kitchen | 1 | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
54 | Haynes Elementary School | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Women’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
55 | Haynes Elementary School | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Men's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
56 | Haynes Elementary School | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Corridor by Gym | 1 | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
57 | Haynes Elementary School | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Grade 1 | 1 | 21 | Priority 3 | Additional Access | Secure rainbow colored mat. | 1 | 0
58 | Haynes Elementary School | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Spanish | 1 | 23 | Priority 3 | Additional Access | Secure the carpet with the map on it. | 1 | 0
59 | Haynes Elementary School | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Corridor by Spanish | 1 | 23 | Priority 3 | Additional Access | Secure the mat. | 1 | 0
60 | Haynes Elementary School | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Kindergarten | 1 | 6 | Priority 3 | Additional Access | Secure the mat. | 1 | 0
61 | Haynes Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Women’s Toilet Room by Lobby and Library | 1 | N/A | Priority 3 | Additional Access | Relocate desk. | 1 | 0
62 | Haynes Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | ESL/LLI | 1 | N/A | Priority 3 | Additional Access | Relocate shelving unit that is by the door. | 1 | 0
63 | Haynes Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Speech Language & Counseling | 1 | N/A | Priority 3 | Additional Access | Relocate bookshelf to provide 60" min deep clear at door. | 1 | 0
64 | Haynes Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Speech Language & Counseling Waiting Room | 1 | N/A | Priority 3 | Additional Access | Relocate desk to provide maneuvering clearance at door. | 1 | 0
65 | Haynes Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Partners Program (Grades 3-5) Classroom Door | 1 | 8 | Priority 3 | Additional Access | Relocate fridge. | 1 | 0
66 | Haynes Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Partners Program (Grades 3-5) Toilet Room | 1 | 8 | Priority 3 | Additional Access | Relocate storage boxes. | 1 | 0
67 | Haynes Elementary School | C. Doors, Doorways, & Gates | D. Maneuvering clearance not provided at recess > 6” | Psychologist Office Exit to Corridor | 1 | N/A | Priority 3 | Additional Access | Install an automatic door opener. | 1 | 3060
68 | Haynes Elementary School | E. Stairways | C. Handrail not provided on both sides | Library | 1 | N/A | Priority 3 | Additional Access | Provide handrails on both sides. | 1 | 1320
69 | Haynes Elementary School | E. Stairways | C. Handrail not provided on both sides | Auditorium/ Cafeteria | 1 | N/A | Priority 3 | Additional Access | Provide handrails on both sides. | 1 | 880
70 | Haynes Elementary School | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Health Office Lobby From Corridor | 1 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
71 | Haynes Elementary School | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | Partners Program (Grades 3-5) | 1 | 8 | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
72 | Haynes Elementary School | H. Signage | Z. Sign lacks 18" min. by 18" min. clear floor space | Principal's Office | 1 | N/A | Priority 2 | Navigational Issue | Relocate folder storage. | 1 | 0
73 | Haynes Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Principal's Office | 1 | N/A | Priority 1 | Program Access | Provide at least 1 work surface with 27" min. knee and toe clearance. Table lacks toe clearance. | 1 | 700
74 | Haynes Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Vice Principal's Office | 1 | N/A | Priority 1 | Program Access | Provide at least 1 work surface with 27" min. knee and toe clearance that is 30" wide, min. | 1 | 700
75 | Haynes Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Psychologist Office | 1 | N/A | Priority 1 | Program Access | Provide at least 1 work surface that has a clear width of 30" min. and a clear height of 24" min. | 1 | 700
76 | Haynes Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | ESL/LLI | 1 | N/A | Priority 1 | Program Access | Ensure that 1 work surface is adjusted to provide 24" min. knee and toe clearance. | 1 | 0
77 | Haynes Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Speech Language & Counseling | 1 | N/A | Priority 1 | Program Access | Provide at least 1 work surface with 27" min. knee and toe clearance that is 30" wide min. | 1 | 700
78 | Haynes Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | OT/PT | 1 | N/A | Priority 1 | Program Access | Provide at least 1 work surface with 24" high min. knee and toe clearance that is 30" wide min. | 1 | 200
79 | Haynes Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Grade 2 | 1 | 19 | Priority 1 | Program Access | Ensure that 1 work surface is adjusted to provide 24" high min. knee and toe clearance. | 1 | 0
80 | Haynes Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Grade 1 | 1 | 21 | Priority 1 | Program Access | Ensure that 1 work surface is adjusted to provide 24" high min. knee and toe clearance. | 1 | 0
81 | Haynes Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Spanish | 1 | 23 | Priority 1 | Program Access | Ensure that 1 work surface is adjusted to provide 24" high min. knee and toe clearance. | 1 | 0
82 | Haynes Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Learning Center for K-3 | 1 | 27 | Priority 1 | Program Access | Provide at least 1 work surface with knee clearance that is 30" wide min. | 1 | 200
83 | Haynes Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Learning Center for K-3 | 1 | 27 | Priority 1 | Program Access | Provide at least 1 dining or work surface with 24" high min. knee and toe clearance. | 1 | 200
84 | Haynes Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Kindergarten | 1 | 6 | Priority 1 | Program Access | Ensure that 1 work surface is adjusted to provide 24" high min. knee and toe clearance. | 1 | 0
85 | Haynes Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Partners Program (Grades 3-5) | 1 | 8 | Priority 1 | Program Access | Provide at least 1 work surface with 24" high min. knee and toe clearance that is 30" wide min. | 1 | 200
86 | Haynes Elementary School | N. Assembly Area | P. Assistive listening devices not provided | Auditorium/ Cafeteria | 1 | N/A | Priority 1 | Program Access | If audible communication is integral to the use of the space, provide an assistive listening system. (Cost estimate for 600 people.) | 1 | 6250
87 | Haynes Elementary School | S. Picnic Tables | G. Toe or knee clearance at tables not provided | Picnic Table and Bench Area | Exterior | N/A | Priority 1 | Program Access | Provide at least 1 dining surface (or ensure that 5% of dining surfaces) have toe and knee clearance. | 1 | 1400
88 | Haynes Elementary School | S. Picnic Tables | H. Picnic table not on an accessible route | Picnic Table with Chess Board | Exterior | N/A | Priority 1 | Program Access | Ensure that the accessible picnic table is connected to an accessible route. (Cost estimate for a 6' long by 4' wide asphalt route.) | 1 | 240
89 | Haynes Elementary School | T. Exterior Benches | A. No accessible route to one bench in area | Seating Area by Birdbath on Northeast Side by the Main Entrance | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to one bench in this area. (Cost estimate for 30' long, 4' wide asphalt route.) | 1 | 1200
90 | Haynes Elementary School | B. Lavatory | B. Toe or knee clearances not provided | Accessible Toilet Room | 1 | N/A | Priority 1 | Program Access | Provide at least one lavatory with knee and toe clearance positioned for a forward approach. As the rest of this toilet room is built to adult dimensions, 27" min. knee clearance is recommended at the lavatory. | 1 | 1686
91 | Haynes Elementary School | B. Lavatory | B. Toe or knee clearances not provided | Kindergarten Toilet Room | 1 | 6 | Priority 1 | Program Access | Provide at least one lavatory with knee and toe clearance positioned for a forward approach. | 1 | 1686
92 | Haynes Elementary School | B. Lavatory | E. Plumbing underneath is exposed | Men’s Toilet Room | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact for at least one lavatory. | 1 | 92
93 | Haynes Elementary School | C. Single-User Toilet | L. Clearance at toilet < 72" clear depth M. Toilet paper dispenser is not compliant Z. Paper towel mounted over grab bar | Accessible Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate shelving and storage. Relocate toilet paper so that it is 24" min. high, located under the grab bar, and between 7" and 9" from the front of the toilet. Relocate the paper towel dispenser so that it is not mounted above the grab bar. | 2 | 706
94 | Haynes Elementary School | C. Single-User Toilet | M. Toilet paper dispenser is not compliant K. Clearance at toilet < 60" clear width | Health Office Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate storage bin. Relocate toilet paper so that it is 24" min. high, located under the grab bar, and between 7" and 9" from the front of the toilet. | 1 | 353
95 | Haynes Elementary School | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Men’s Toilet Room | 1 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
96 | Haynes Elementary School | F. Dispensers | D. Dispenser acts as a protruding object | Health Office Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate dispenser out of the circulation path. | 1 | 353
97 | Haynes Elementary School | F. Dispensers | D. Dispenser acts as a protruding object | Women’s Toilet Room by Lobby and Library and Men's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate paper towel dispenser out of the circulation path. | 2 | 706
98 | Haynes Elementary School | A. Single-User Toilet (Children) | A. Clearance at toilet < 72" clear deep | Partners Program (Grades 3-5)Toilet Room | 1 | 8 | Priority 3 | Additional Access | Relocate stored items so that there is 72" clear deep at the toilet. | 1 | 0
99 | Haynes Elementary School | A. Single-User Toilet (Children) | Q. Non-compliant toilet paper dispenser | Kindergarten Toilet Room | 1 | 6 | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars. | 1 | 353
100 | Haynes Elementary School | A. Single-User Toilet (Children) | R. Coat hook not within reach range | Health Office Toilet Room | 1 | N/A | Priority 3 | Additional Access | Lower hook so that it is no higher than 40" above the floor. | 1 | 150
101 | Haynes Elementary School | B. Toilet Compartment (Children) | R. Non-compliant toilet paper dispenser | Girls' Toilet Room Across From Auditorium | 1 | N/A | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars. | 1 | 353
102 | Haynes Elementary School | B. Toilet Compartment (Children) | R. Non-compliant toilet paper dispenser U. Coat hook not within reach range | Women’s Toilet Room by Lobby and Library | 1 | N/A | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars. Lower hook so that it is no higher than 44" for children ages 9-12. The other dimensions in the toilet room are built for this age range. | 1 | 503
103 | Haynes Elementary School | B. Toilet Compartment (Children) | R. Non-compliant toilet paper dispenser U. Coat hook not within reach range | Men's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars. Lower hook so that it is no higher than 44" for children ages 9-12. The other dimensions in the toilet room are built for this age range. | 1 | 503
104 | Haynes Elementary School | B. Toilet Compartment (Children) | R. Non-compliant toilet paper dispenser U. Coat hook not within reach range | Boys' Toilet Room by Health Office | 1 | N/A | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars. Lower hook so that it is no higher than 44" for children ages 9-12. The rest of the dimensions in this toilet room are for this age group. | 1 | 503
105 | Haynes Elementary School | C. Lavatory (Children) | A. Toe or knee clearances not provided | Partners Program (Grades 3-5)Toilet Room | 1 | 8 | Priority 1 | Program Access | Provide at least one lavatory with 25" min. knee clearance positioned for a forward approach. | 1 | 1686
106 | Haynes Elementary School | C. Lavatory (Children) | A. Toe or knee clearances not provided | Partners Program (Grades K-2)Toilet Room | 1 | 9 | Priority 1 | Program Access | Provide at least one lavatory with 25" min. knee clearance positioned for a forward approach. | 1 | 1686
107 | Haynes Elementary School | C. Lavatory (Children) | E. Exposed plumbing underneath | Boys' Toilet Room by Health Office | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at lavatory. | 1 | 92
108 | Haynes Elementary School | C. Lavatory (Children) | E. Exposed plumbing underneath | Girls' Toilet Room Across From Auditorium | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at lavatory. | 1 | 92
109 | Haynes Elementary School | C. Lavatory (Children) | E. Exposed plumbing underneath | Health Office Toilet Room | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at lavatory. | 1 | 92
109 | Haynes Elementary School | C. Lavatory (Children) | F. Mirror above lavatory w/reflective surface > 31" | Health Office Toilet Room | 1 | N/A | Priority 3 | Additional Access | Lower mirror so that the bottom surface is at 31" above finished floor. | 1 | 256
110 | Haynes Elementary School | D. Dispensers (Children) | A. Dispenser controls > 42" high | Boys' Toilet Room by Health Office | 1 | N/A | Priority 3 | Additional Access | Relocate so the operable part is 42" max. above the finished floor. | 1 | 353
111 | Haynes Elementary School | E. Urinal (Children) | B. Urinal has < 30" clear width D. Urinal recessed > 24" deep has > 36" clear width | Boys' Toilet Room by Health Office | 1 | N/A | Priority 1 | Program Access | Remove partition to provide a 30" min. by 48" min. clear floor space positioned for a forward approach. Provide a partition that is less than 24" deep. | 1 | 353
112 | Haynes Elementary School | F. Toilet Paper Dispensers (Children) | C. Controls < 14" or > 17" (Ages 5 - 8) E. Dispenser located above grab bar | Partners Program (Grades K-2)Toilet Room | 1 | 9 | Priority 3 | Additional Access | Relocate toilet paper dispenser so the operable part is between 14" and 17" above the finished floor. Relocate dispenser 1.5" minimum underneath the grab bar. | 1 | 353
113 | Haynes Elementary School | F. Toilet Paper Dispensers (Children) | D. Controls < 17" or > 19" (Ages 9 - 12) E. Dispenser located above grab bar | Partners Program (Grades 3-5)Toilet Room | 1 | 8 | Priority 3 | Additional Access | Relocate toilet paper dispenser so the operable part is between 14" and 17" above the finished floor. Relocate dispenser 1.5" minimum underneath the grab bar. | 1 | 353
114 | Haynes Elementary School | A. Drinking Fountains | B. Clear floor space not provided C. Operable parts malfunctioning H. No drinking fountain provided for standing users | Exit From Corridor by Rooms 22 and 23 | Exterior | N/A | Priority 3 | Additional Access | Provide a 30" by 48" clear floor space positioned for a forward approach. (Cost estimate for 3' by 4' asphalt area.) Repair or replace drinking fountain to ensure operable parts are functioning. Provide an additional drinking fountain for standing users on an accessible route. | 1 | 4148
115 | Haynes Elementary School | A. Drinking Fountains | H. No drinking fountain provided for standing users | Drinking Fountain | 1 | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users. | 1 | 4028
116 | Haynes Elementary School | A. Drinking Fountains | H. No drinking fountain provided for standing users | Drinking Fountain by Gym | 1 | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users. | 1 | 4028
117 | Haynes Elementary School | A. Drinking Fountains | H. No drinking fountain provided for standing users L. Knee or toe clearance not provided | Drinking Fountain | 1 | N/A | Priority 1 | Program Access | Install a Hi-Lo drinking fountain. | 1 | 4216
118 | Haynes Elementary School | A. Drinking Fountains | L. Knee or toe clearance not provided | Drinking Fountain by Women’s Toilet Room | 1 | N/A | Priority 1 | Program Access | Provide a drinking fountain with knee and toe clearance, 27" min. high at drinking fountain for seated users. (Cost for a new low drinking fountain.) | 1 | 4028
119 | Haynes Elementary School | B. Sink | B. Toe and knee clearances not provided E. Exposed plumbing underneath sink | Health Office | 1 | N/A | Priority 1 | Safety | Ensure there is a 27" knee clearance positioned for a forward approach. Insulate or otherwise configure pipes at sink. | 1 | 1778
120 | Haynes Elementary School | B. Sink | B. Toe and knee clearances not provided E. Exposed plumbing underneath sink G. Dispenser not within reach range | Learning Lab | 1 | N/A | Priority 1 | Safety | Ensure there is a 27" knee clearance positioned for a forward approach. Insulate or otherwise configure pipes at sink. Relocate paper towel dispenser 44" max. above the finished floor or ground. | 1 | 2034
121 | Haynes Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | OT/PT | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
122 | Haynes Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Music Room | 1 | 1 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
123 | Haynes Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Grade 4 | 1 | 13 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
124 | Haynes Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Learning Center for Grades 4-5 | 1 | 15 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
125 | Haynes Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Grade 5 | 1 | 16 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
126 | Haynes Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Grade 2 | 1 | 19 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
127 | Haynes Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Grade 3 | 1 | 2 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
128 | Haynes Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Grade 1 | 1 | 21 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
129 | Haynes Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Spanish | 1 | 23 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
130 | Haynes Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Steps Room | 1 | 25 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
131 | Haynes Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Learning Center for K-3 | 1 | 27 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
132 | Haynes Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Partners Program (Grades 3-5) | 1 | 8 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
133 | Haynes Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Partners Program (Grades K-2) | 1 | 9 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
134 | Haynes Elementary School | C. Sinks for Children's Use | D. Knee or toe clearance not provided | Auditorium/ Cafeteria | 1 | N/A | Priority 1 | Program Access | Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1686
135 | Haynes Elementary School | C. Sinks for Children's Use | D. Knee or toe clearance not provided | Art Classroom | 1 | 11 | Priority 1 | Program Access | Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1686
136 | Haynes Elementary School | C. Sinks for Children's Use | D. Knee or toe clearance not provided | Kindergarten | 1 | 6 | Priority 1 | Program Access | Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1686
137 | Haynes Elementary School | B. Play Areas | A. Accessible route not provided to playground B. Accessible route not provided around playground C. Accessible route not provided to play components | Swing Sets North of the Basketball Court | Exterior | N/A | Priority 1 | Program Access | Install an accessible route to and around the playground. (Cost estimate for 430' long, 4' wide asphalt route.) Provide a compliant impact-attenuating surface to and around the play components. (Cost estimate for 1,380 sq. ft. of poured in place rubber surface.) | 1 | 36520
138 | Haynes Elementary School | B. Play Areas | B. Accessible route not provided around playground C. Accessible route not provided to play components | Southwest Playground | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route around the play area. (Cost estimate for 144' long 4' wide asphalt route, including a route to the bench.) Provide a compliant impact-attenuating surface to and around the play components. (Cost estimate for 1,344 sq. ft. of poured in place rubber surface.) | 1 | 24576
139 | Haynes Elementary School | C. Field | C. Field not connected to an accessible route | Soccer Field | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to each soccer field. (Cost estimate for 80' long by 4' wide stone dust route.) | 1 | 2560
140 | Haynes Elementary School | C. Field | C. Field not connected to an accessible route | Baseball Field | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the field. (Cost estimate for 60' long, 4' wide asphalt route.) | 1 | 2400
141 | Haynes Elementary School | N/A | N/A | Accessible Shower Across From Health Office | 1 | 14 |  |  | Note: Shower room was unable to be surveyed. | 1 | 0
142 | Haynes Elementary School | N/A | N/A | Lead Teacher Office, Vice Principal's Office, Psychologist Office | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing a sign at all permanent rooms where a sign is not provided. | 3 | 0
143 | Haynes Elementary School | N/A | N/A | Auditorium/ Cafeteria | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing a sign at all permanent rooms where a sign is not provided. | 1 | 0
144 | Haynes Elementary School | N/A | N/A | Corridor Stairs to Stage | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing designation signage with raised characters and braille at all permanent rooms lacking signage. Recommend providing directional signage to the accessible route to the stage. | 1 | 0
145 | Haynes Elementary School | N/A | N/A | Stage Ramp Door Across From Music Room | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing designation signage with raised characters and braille at all permanent rooms lacking signage. | 1 | 0
146 | Haynes Elementary School | N/A | N/A | ESL/LLI | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing designation signage with raised characters and braille at all permanent rooms lacking signage. | 1 | 0
147 | Haynes Elementary School | N/A | N/A | Corridor | 1 | N/A | Priority 4 | Enhanced Usability | Recommend locating some hooks in the main corridor within recommended children's reach ranges between 40" and 44" high for students in the kindergarten through the fifth grade. | 1 | 0
148 | Haynes Elementary School | N/A | N/A | Learning Center Storage Shelves for K-3 | 1 | 27 |  |  | It is good example to see height adjustable shelving. | 1 | 0
149 | Haynes Elementary School | N/A | N/A | Partners Program (Grades 3-5) | 1 | 8 |  |  | Individual workspaces for children can fold down behind cubicle walls. This feature is very useful for students with learning disabilities. | 1 | 0
150 | Haynes Elementary School | N/A | N/A | Exit Door 16 | Ext | 13 | Priority 4 | Enhanced Usability | Recommend providing an accessible walkway from each ground level classroom exit door. | 1 | 0
151 | Haynes Elementary School | N/A | N/A | Southwest Playground Gate | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a 10" high solid surface kickplate on the push side of the gate to the southwest playground. | 1 | 0
152 | Haynes Elementary School | N/A | N/A | Swing Sets North of the Basketball Court | Exterior | N/A |  |  | Good example to see a variety of swings in this swingset area. | 1 | 0
153 | Haynes Elementary School | N/A | N/A | Picnic Table With Chess Board | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a 48" wide accessible route around entire picnic table at each accessible picnic table. | 1 | 0
154 | Haynes Elementary School | N/A | N/A | Seating Area by Birdbath on Northeast Side by the Main Entrance | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a 36" x 48" space alongside one bench positioned so that a person using a wheelchair can sit shoulder to shoulder with someone seated on the bench. Recommend providing a variety of benches, including benches with backs and armrests. | 1 | 0
1 | Loring Elementary School | A. Exterior Access Route | F. Surface openings > 1/2" | Near Gymnasium | Exterior | N/A | Priority 3 | Additional Access | Repair opening. (Cost based on a 4'x4' concrete patch.) | 1 | 256
2 | Loring Elementary School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Courtyard | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). (Cost base on 15' of asphalt to correct slope.) | 1 | 600
3 | Loring Elementary School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | From Main Entrance Towards Exit 11 | Exterior | N/A | Priority 1 | Program Access | Reduce cross slope to be no steeper than 1:50 (2.00%). (Cost for 4'x15 of asphalt to correct slope.) | 1 | 600
4 | Loring Elementary School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | From Main Entrance Towards Exit 11 | Exterior | N/A | Priority 1 | Program Access | Reduce cross slope to be no steeper than 1:50 (2.00%). (Cost for 4'x6' of asphalt to correct slope.) | 1 | 240
5 | Loring Elementary School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | From Exit 10 To Exit 8 | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). (Cost based on 4'x6' of asphalt to correct slope.) | 1 | 240
6 | Loring Elementary School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | From Exit 8 Towards Basketball Court | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). (Cost based on 4'x6' of asphalt to correct slope.) | 1 | 240
7 | Loring Elementary School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Walkway | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). | 1 | 240
8 | Loring Elementary School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Walkway | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). | 1 | 240
9 | Loring Elementary School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Walkway | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). | 1 | 240
10 | Loring Elementary School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Walkway | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). | 1 | 240
11 | Loring Elementary School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Walkway Across From Main Entrance | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). | 1 | 240
12 | Loring Elementary School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) H. Running slope > 1:20 (5%) | Path to Basketball Court/Upper Playground | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). Reduce running slope to be no steeper than 1:20 (5%). (Cost based on 4'x6' of asphalt to correct slope.) | 1 | 240
13 | Loring Elementary School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) M. Route not maintained in operable working condition | From Exit 11 Towards Exit 10 | Exterior | N/A | Priority 1 | Program Access | Reduce cross slope to be no steeper than 1:50 (2.00%). Ensure the accessible route is maintained in operable working condition. (Cost for 4'x6' of asphalt to correct slope and repair surface opening.) | 1 | 240
14 | Loring Elementary School | A. Exterior Access Route | H. Running slope > 1:20 (5%) | Path to Basketball Court/Upper Playground | Exterior | N/A | Priority 3 | Additional Access | Reduce running slope to be no steeper than 1:20 (5%). (Cost based on 4'x6' of asphalt to correct slope.) | 1 | 240
15 | Loring Elementary School | A. Exterior Access Route | J. Level changes > 1/4" | Courtyard to Lobby Entrance | Exterior | N/A | Priority 1 | Program Access | Alter change in level to be 1/4" high max. (Cost based on a 4'x4' asphalt patch.) | 1 | 160
16 | Loring Elementary School | A. Exterior Access Route | J. Level changes > 1/4" | Curb Ramp Opposite Exit 10 | Exterior | N/A | Priority 1 | Program Access | Alter change in level to be 1/4" high max. (Cost based on a concrete patch.) | 1 | 256
17 | Loring Elementary School | A. Exterior Access Route | J. Level changes > 1/4" | From Exit 10 To Exit 8 | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. (Cost based on 2'x10 of beveled asphalt to reduce change in level.) | 1 | 200
18 | Loring Elementary School | A. Exterior Access Route | J. Level changes > 1/4" | Exit 8 | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. (Cost based on an asphalt patch.) | 1 | 160
19 | Loring Elementary School | A. Exterior Access Route | J. Level changes > 1/4" | Curb Ramp at Basketball Court | Exterior | N/A | Priority 1 | Program Access | Alter change in level to be 1/4" high max. (Cost based on asphalt patch to correct change in level.) (Cost included in ID #37 - Cost for a new compliant curb ramp.) | 1 | 0
20 | Loring Elementary School | A. Exterior Access Route | J. Level changes > 1/4" | Small Gate Entry to Basketball Court/Upper Playground | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. (Cost for an asphalt patch.) | 1 | 160
21 | Loring Elementary School | A. Exterior Access Route | J. Level changes > 1/4" | Curb Ramp at Basketball Court | Exterior | N/A | Priority 1 | Program Access | Alter change in level to be 1/4" high max. (Cost based on asphalt patch to correct change in level.) (Cost included in ID #37 - Cost for a new compliant curb ramp.) | 1 | 0
22 | Loring Elementary School | A. Exterior Access Route | J. Level changes > 1/4" N. Accessible route not provided | Door 9 | Exterior | N/A | Priority 1 | Program Access | Alter change in level to be 1/4" high max. Ensure an accessible route is provided. (Cost based on an asphalt patch.) | 1 | 160
23 | Loring Elementary School | A. Exterior Access Route | M. Route not maintained in operable working condition | Door 8 | Exterior | N/A | Priority 1 | Program Access | Ensure the accessible route is maintained in operable working condition. Repair 2" gap with asphalt patch. | 1 | 160
24 | Loring Elementary School | A. Exterior Access Route | M. Route not maintained in operable working condition | From Main Entrance Towards Exit 11 | Exterior | N/A | Priority 1 | Program Access | Ensure the accessible route is maintained in operable working condition. Repair deteriorated asphalt. | 1 | 160
25 | Loring Elementary School | A. Exterior Access Route | M. Route not maintained in operable working condition | From Exit 10 To Exit 8 | Exterior | N/A | Priority 1 | Program Access | Ensure the accessible route is maintained in operable working condition. Repair deteriorated asphalt. (Cost based on an asphalt patch.) | 1 | 160
26 | Loring Elementary School | A. Exterior Access Route | M. Route not maintained in operable working condition | Path to Basketball Court/Upper Playground | Exterior | N/A | Priority 1 | Program Access | Ensure the accessible route is maintained in operable working condition. (Cost based on 4'x4' of asphalt to repair surface.) | 1 | 160
27 | Loring Elementary School | A. Exterior Access Route | M. Route not maintained in operable working condition | Entry to Basketball Court/Upper Playground | Exterior | N/A | Priority 1 | Program Access | Ensure the accessible route is maintained in operable working condition. Repair surface at gate to basketball court. (Cost based on an asphalt patch.) | 1 | 160
28 | Loring Elementary School | A. Exterior Access Route | N. Accessible route not provided | Garden Box | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided to the garden box. (Cost based on a 4' wide min. x 6' long stone dust path from existing walkway to garden box.) | 1 | 192
29 | Loring Elementary School | B. Curb Ramp | A. Curb ramp not provided D. Running slope > 1:12 (8.33%) F. Handrails not provided at both sides if rise is > 6" | Exit From Cafeteria | Exterior | N/A | Priority 1 | Program Access | Provide a curb ramp at intersection. Provide a handrail on both sides. (Cost estimate for a new concrete curb ramp and 30' of metal handrail.) | 1 | 5020
30 | Loring Elementary School | B. Curb Ramp | D. Running slope > 1:12 (8.33%) | Crosswalk Near Woodside Road | Exterior | N/A | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:12 (8.33%). (Cost estimate for a new concrete curb ramp.) | 1 | 2800
31 | Loring Elementary School | B. Curb Ramp | D. Running slope > 1:12 (8.33%) E. Transition from curb ramp to street not flush F. Curb ramp flares > 1:10 (10%) | Curb Ramp 2 Near Basketball Court | Exterior | N/A | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:12 (8.33%). Ensure transition from curb ramp to street is flush or free of changes in level. Reduce slope at curb ramp flares to be no steeper than 1:10 (10%). (Cost estimate for a new concrete curb ramp.) | 1 | 2800
32 | Loring Elementary School | B. Curb Ramp | D. Running slope > 1:12 (8.33%) J. Landing not provided at top of curb ramp | Crosswalk Near Woodside Road | Exterior | N/A | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:12 (8.33%). Provide landing at top of curb ramp or reconfigure ramp. (Cost estimate for a new concrete curb ramp.) | 1 | 2800
33 | Loring Elementary School | B. Curb Ramp | E. Transition from curb ramp to street not flush | Curb Ramp at Basketball Court | Exterior | N/A | Priority 1 | Program Access | Ensure transition from curb ramp to street is flush or free of changes in level. (Cost included in ID #37 - Cost for a new compliant curb ramp.) | 1 | 0
34 | Loring Elementary School | B. Curb Ramp | E. Transition from curb ramp to street not flush | Curb Ramp at Basketball Court | Exterior | N/A | Priority 1 | Program Access | Ensure transition from curb ramp to street is flush or free of changes in level. (Cost included in ID #37 - Cost for a new compliant curb ramp.) | 1 | 0
35 | Loring Elementary School | B. Curb Ramp | E. Transition from curb ramp to street not flush | Curb Ramp at Basketball Court | Exterior | N/A | Priority 1 | Program Access | Ensure transition from curb ramp to street is flush or free of changes in level. (Cost included in ID #37 - Cost for a new compliant curb ramp.) | 1 | 0
36 | Loring Elementary School | B. Curb Ramp | F. Curb ramp flares > 1:10 (10%) | Curb Ramp Opposite Exit 10 | Exterior | N/A | Priority 1 | Program Access | Reduce slope at up hill curb ramp flare to be no steeper than 1:10 (10%). (Cost estimate for concrete to reduce slope.) | 1 | 256
37 | Loring Elementary School | B. Curb Ramp | J. Landing not provided at top of curb ramp S. Cross slope > 1:50 (2%) (MAAB) | Curb Ramp at Basketball Court | Exterior | N/A | Priority 1 | Program Access | Provide a 5'x5' landing at top of curb ramp. Reduce cross slope at curb ramp to be no steeper than 1:50 (2%). (Cost for a new compliant concrete curb ramp addressing all shown curb ramp issues.) | 1 | 2800
38 | Loring Elementary School | C. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces C. Total # of designated van accessible spaces N. Sign not provided O. Sign does not have the designation "Van Accessible" | By Baseball Field | Exterior | N/A | Priority 1 | Program Access | Provide one compliant van accessible parking space and access aisle each 8' wide min. (re-stripe). Provide a sign with the International Symbol of Accessibility with the bottom of the sign 60" min. above the ground and the top 96" max. above the ground. Add the designation "Van Accessible" to the sign located at the van accessible space. | 1 | 800
39 | Loring Elementary School | C. Off-Street Parking Lot or Garage | B. Total # of designated accessible parking spaces C. Total # of designated van accessible spaces O. Sign does not have the designation "Van Accessible" | Accessible Parking Opposite Exit 11 and 10 | Exterior | N/A | Priority 1 | Program Access | Add the designation "Van Accessible" to the sign located at the van accessible space (the space furthest to the right in this photograph). Ensure there is at least 60" clear height measured to the bottom of the sign. | 1 | 500
40 | Loring Elementary School | F. Exterior Stair | N/A | Staircase Lower Level | Exterior | N/A | Priority 3 | Additional Access | Note: IHCD confirmed that the slopes at the bottom landing of the stairs leading to the lower playground are compliant, and IHCD has been told that the stairs will remain for reasons related to public safety. | 1 | 0
41 | Loring Elementary School | F. Exterior Stair | O. Not maintained in operable working condition | Staircase to Lower Playground | Exterior | N/A | Priority 3 | Additional Access | Ensure stairs are maintained in operable working condition. The third step from the top, the third step from the middle landing and the last step at the bottom show some chipping and deterioration. Repair surface. | 1 | 0
42 | Loring Elementary School | A. Means of Egress | B. Tactile exit sign not provided | Egress Door 9 | 1 | 154 | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. | 1 | 232
43 | Loring Elementary School | A. Means of Egress | B. Tactile exit sign not provided | Egress Door 10 | 1 | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. | 1 | 232
44 | Loring Elementary School | A. Means of Egress | B. Tactile exit sign not provided | Egress Door 11 | 1 | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. | 1 | 232
45 | Loring Elementary School | A. Means of Egress | B. Tactile exit sign not provided O. Illuminated ISA symbol not provided (MAAB) | Main Entrance and Egress Door 1 | 1 | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
46 | Loring Elementary School | A. Means of Egress | B. Tactile exit sign not provided O. Illuminated ISA symbol not provided (MAAB) | Cafetorium Egress | 1 | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
47 | Loring Elementary School | A. Means of Egress | B. Tactile exit sign not provided O. Illuminated ISA symbol not provided (MAAB) | Door 6 at Gymnasium | 1 | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
48 | Loring Elementary School | A. Means of Egress | B. Tactile exit sign not provided O. Illuminated ISA symbol not provided (MAAB) | Egress Door 7 | 1 | 154 | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
49 | Loring Elementary School | A. Means of Egress | B. Tactile exit sign not provided O. Illuminated ISA symbol not provided (MAAB) | Egress Door 8 | 1 | 154 | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
50 | Loring Elementary School | B. Interior Access Route | A. Route < 36" wide | Assistant Principle | 1 | 102 | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. | 1 | 0
51 | Loring Elementary School | B. Interior Access Route | A. Route < 36" wide | Cafetorium | 1 | N/A | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. (Width decreases at extended counter. If students walk past that counter, maintain 36" min. clear width.) | 1 | 0
52 | Loring Elementary School | B. Interior Access Route | A. Route < 36" wide | Music Practice | 1 | 164 | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. | 1 | 0
53 | Loring Elementary School | B. Interior Access Route | A. Route < 36" wide | Work Room | 1 | N/A | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. | 1 | 0
54 | Loring Elementary School | B. Interior Access Route | A. Route < 36" wide | Special Education | 1 | 159 | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. | 1 | 0
55 | Loring Elementary School | B. Interior Access Route | A. Route < 36" wide | Classroom 235 | 2 | 235 | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. | 1 | 0
56 | Loring Elementary School | C. Doors, Doorways, & Gates | A. Clear width at door < 32" | Small Gate Entry to Basketball Court/Upper Playground | Exterior | N/A | Priority 3 | Additional Access | Widen the gate so that there is 32" min. clear width. | 1 | 0
57 | Loring Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Room 107 | 1 | 107 | Priority 3 | Additional Access | Remove chair to provide 18" min. pull-side maneuvering clearance at door. | 1 | 0
58 | Loring Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Room 110 | 1 | 110 | Priority 3 | Additional Access | Remove stored items to provide 18" min. pull-side maneuvering clearance at door. | 1 | 0
59 | Loring Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Boys' Toilet Room | 1 | 167 | Priority 3 | Additional Access | Remove the trash can to provide 18" min. pull-side maneuvering clearance at door. | 1 | 0
60 | Loring Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Girls' Toilet Room | 1 | 168 | Priority 3 | Additional Access | Remove the trash can to provide 18" min. pull-side maneuvering clearance at door. | 1 | 0
61 | Loring Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Psychologist's Office | 1 | N/A | Priority 3 | Additional Access | Remove stored objects to provide 18" min. pull-side maneuvering clearance at door. | 1 | 0
62 | Loring Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Kindergarten | 1 | 135 | Priority 3 | Additional Access | Remove trash cans to provide 18" min. pull-side maneuvering clearance at the door. | 1 | 0
63 | Loring Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Spanish Classroom Single-User Toilet Room | 1 | 133 | Priority 3 | Additional Access | Remove shelving to provide 18" min. pull-side maneuvering clearance at door. | 1 | 0
64 | Loring Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Men's Toilet Room | 1 | 127 | Priority 3 | Additional Access | Remove the trash can to provide 18" min. pull-side maneuvering clearance at the door. | 1 | 0
65 | Loring Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Learning Center | 1 | 115 | Priority 3 | Additional Access | Remove stored items to provide 18" min. pull-side maneuvering clearance at the door. | 1 | 0
66 | Loring Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Guidance Office Suite | 1 | 113 | Priority 3 | Additional Access | Remove stored items to provide 18" min. pull-side maneuvering clearance at the door. | 1 | 0
67 | Loring Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Grade 2 Classroom | 2 | 233 | Priority 3 | Additional Access | Remove trash cans to provide 18" min. pull-side maneuvering clearance at the door. | 1 | 0
68 | Loring Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Boys' Toilet Room | 2 | 227 | Priority 3 | Additional Access | Remove the trash can to provide 18" min. pull-side maneuvering clearance at the door. | 1 | 0
69 | Loring Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Girls' Toilet Room | 2 | 226 | Priority 3 | Additional Access | Remove the trash can to provide 18" min. pull-side maneuvering clearance at the door. | 1 | 0
70 | Loring Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Grade 4 Classroom | 2 | 216 | Priority 3 | Additional Access | Remove the trash can to provide 18" min. pull-side maneuvering clearance at the door. | 1 | 0
71 | Loring Elementary School | C. Doors, Doorways, & Gates | H. Mat not securely attached | Main Entrance Door 1 | Exterior | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
72 | Loring Elementary School | C. Doors, Doorways, & Gates | H. Mat not securely attached | Administrative Office | 1 | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
73 | Loring Elementary School | C. Doors, Doorways, & Gates | H. Mat not securely attached | Cafetorium | 1 | 185 | Priority 3 | Additional Access | Secure the mat. | 1 | 0
74 | Loring Elementary School | C. Doors, Doorways, & Gates | H. Mat not securely attached | Hallway | 1 | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
75 | Loring Elementary School | C. Doors, Doorways, & Gates | H. Mat not securely attached | Cafetorium Egress | 1 | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
76 | Loring Elementary School | C. Doors, Doorways, & Gates | H. Mat not securely attached | Cafetorium Egress | 1 | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
77 | Loring Elementary School | D. Ramps | S. Not maintained in operable working condition | Ramp to Stage | 1 | 189 | Priority 1 | Program Access | Remove stored items from ramp. |  | 0
78 | Loring Elementary School | E. Stairways | N. Not maintained in operable working condition | Stairs to Stage | 1 | 188 | Priority 1 | Program Access | Remove stored items blocking stair landing. | 1 | 0
79 | Loring Elementary School | E. Stairways | P. Handrails not provided | Cafetorium Stage | 1 | N/A | Priority 3 | Additional Access | Provide handrails on at least one side of the stage. (Cost based on 6' of wood railing.) | 1 | 352
80 | Loring Elementary School | K. Operable Parts | B. Clear floor space is not provided | Main Entrance Door 1 | Exterior | N/A | Priority 3 | Additional Access | Keep stored items away from intercom. | 1 | 0
81 | Loring Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Cafetorium | 1 | N/A | Priority 1 | Program Access | Provide at least 1 dining surface with 24" min. knee and toe clearance. | 1 | 1100
82 | Loring Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | PT/OT | 1 | N/A | Priority 1 | Program Access | Provide at least 1 work surface with 24" min. knee and toe clearance. | 1 | 700
83 | Loring Elementary School | N. Assembly Area | P. Assistive listening devices not provided | Cafetorium Stage | 1 | N/A | Priority 1 | Program Access | If audible communication is integral to the use of the space, provide an assistive listening system. | 1 | 1214
84 | Loring Elementary School | S. Picnic Tables | C. At least 5% accessible spaces not provided | Lower Playground | Exterior | N/A | Priority 1 | Program Access | Ensure that at least 5% (minimum one) of the picnic tables in this area are accessible. (Cost based on a new accessible picnic table.) | 1 | 1400
85 | Loring Elementary School | S. Picnic Tables | G. Toe or knee clearance at tables not provided H. Picnic table not on an accessible route | Courtyard | Exterior | N/A | Priority 1 | Program Access | Provide at least 1 picnic table in this area with toe and knee clearance. Ensure that the dining surface is connected to an accessible route. (Cost based on an accessible picnic table.) | 1 | 1400
86 | Loring Elementary School | T. Exterior Benches | A. No accessible route to one bench in area | Courtyard | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to 20% of benches in this area. (Cost based on a 48" wide min. x 12' long stone dust path with a max. cross slope of 1:50 (2.00%) and a max. running slope of 1:20 (5.00%). | 1 | 384
87 | Loring Elementary School | B. Lavatory | A. Clear floor space not provided at lavatory | Women's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Provide at least one lavatory with a 30" min. by 48" min. clear floor space positioned for a forward approach. (Relocate paper towel dispenser out of clear floor space at lavatory.) | 1 | 353
88 | Loring Elementary School | D. Toilet Compartment | M. Flush control not on open side N. Non-compliant toilet paper dispenser | Men's Toilet Room | 1 | 127 | Priority 3 | Additional Access | Provide the flush control on the open side of the toilet (transfer side). Relocate toilet paper so that it is 24" min. high, located under the grab bar, and between 7" and 9" from the front of the toilet. Replace dispenser as it does not allow continuous paper flow. | 1 | 727
89 | Loring Elementary School | E. Urinal | A. Rim > 17" high | Men's Toilet Room | 1 | 127 | Priority 1 | Program Access | Provide at least one urinal with the rim no higher than 17" above the finished floor. | 1 | 3248
90 | Loring Elementary School | E. Urinal | A. Rim > 17" high | Men's Toilet Room | 2 | 213 | Priority 1 | Program Access | Provide at least one urinal with the rim no higher than 17" above the finished floor. | 1 | 3248
91 | Loring Elementary School | F. Dispensers | D. Dispenser acts as a protruding object | Boys' Toilet Room | 1 | 167 | Priority 3 | Additional Access | Relocate dispenser out of the circulation path or place a cane-detectable barrier under the dispenser. | 1 | 306
92 | Loring Elementary School | F. Dispensers | D. Dispenser acts as a protruding object | Women's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate dispenser out of the circulation path or place a cane-detectable barrier under the dispenser. | 1 | 306
93 | Loring Elementary School | F. Dispensers | D. Dispenser acts as a protruding object | Girls' Toilet Room | 2 | N/A | Priority 3 | Additional Access | Relocate dispenser out of the circulation path or place a cane-detectable barrier under the dispenser. | 1 | 306
94 | Loring Elementary School | F. Dispensers | D. Dispenser acts as a protruding object | Men's Toilet Room | 2 | 213 | Priority 3 | Additional Access | Relocate dispenser out of the circulation path or place a cane-detectable barrier under the dispenser. | 1 | 306
95 | Loring Elementary School | A. Single-User Toilet (Children) | B. Clearance at toilet < 60" clear wide | Single-User Toilet Room | 1 | 109 | Priority 3 | Additional Access | Remove storage cabinet to provide a clear floor space that is 60" wide min. | 1 | 0
96 | Loring Elementary School | A. Single-User Toilet (Children) | D. Flush control not on open side Q. Non-compliant toilet paper dispenser | Spanish Classroom Single-User Toilet Room | 1 | 133 | Priority 3 | Additional Access | Move the flush control to the open side. Mount flush control between 20" - 30" above the floor. Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars. Also relocate the paper towel and soap dispensers from above the grab bar. | 1 | 1433
97 | Loring Elementary School | A. Single-User Toilet (Children) | Q. Non-compliant toilet paper dispenser | Kindergarten Single-User Toilet Room | 1 | 135 | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars./Replace dispenser as it does not allow continuous paper flow. Also relocate the paper towel and soap dispensers from above the grab bar. | 1 | 1058
98 | Loring Elementary School | A. Single-User Toilet (Children) | Q. Non-compliant toilet paper dispenser Paper towel dispenser and tampon dispenser above grab bar. | Single-User Toilet Room | 1 | 109 | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars./Replace dispenser as it does not allow continuous paper flow. Relocate all dispensers so they are not located above the grab bars. (MAAB) | 3 | 900
99 | Loring Elementary School | B. Toilet Compartment (Children) | L. Side or rear grab bar < 25" or > 27" high (Ages 9 - 12) R. Non-compliant toilet paper dispenser | Girls' Toilet Room | 2 | N/A | Priority 3 | Additional Access | Relocate side grab bar to 25"- 27" above the floor. Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars./Replace dispenser as it does not allow continuous paper flow. | 1 | 609
100 | Loring Elementary School | B. Toilet Compartment (Children) | N. Flush control not on open side R. Non-compliant toilet paper dispenser | Boys' Toilet Room | 1 | 147 | Priority 3 | Additional Access | Provide the flush control on the open side of the toilet (transfer side), no higher than 44". Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars./Replace dispenser as it does not allow continuous paper flow. | 1 | 727
101 | Loring Elementary School | B. Toilet Compartment (Children) | N. Flush control not on open side R. Non-compliant toilet paper dispenser | Boys' Toilet Room | 2 | 227 | Priority 3 | Additional Access | Provide the flush control on the open side of the toilet (transfer side), no higher than 44". Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars./Replace dispenser as it does not allow continuous paper flow. | 1 | 1778
102 | Loring Elementary School | B. Toilet Compartment (Children) | R. Non-compliant toilet paper dispenser | Boys' Toilet Room | 1 | 167 | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars./Replace dispenser as it does not allow continuous paper flow. | 1 | 353
103 | Loring Elementary School | B. Toilet Compartment (Children) | R. Non-compliant toilet paper dispenser | Girls' Toilet Room | 1 | 168 | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars./Replace dispenser as it does not allow continuous paper flow. | 1 | 353
104 | Loring Elementary School | B. Toilet Compartment (Children) | R. Non-compliant toilet paper dispenser | Girls' Toilet Room | 1 | 146 | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars./Replace dispenser as it does not allow continuous paper flow. | 1 | 353
105 | Loring Elementary School | B. Toilet Compartment (Children) | R. Non-compliant toilet paper dispenser | Women's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars. Replace dispenser as it does not allow continuous paper flow. | 1 | 353
106 | Loring Elementary School | B. Toilet Compartment (Children) | R. Non-compliant toilet paper dispenser | Boys' Toilet Room | 2 | 241 | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars./Replace dispenser as it does not allow continuous paper flow. | 1 | 353
107 | Loring Elementary School | B. Toilet Compartment (Children) | R. Non-compliant toilet paper dispenser | Girls' Toilet Room | 2 | 226 | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars./Replace dispenser as it does not allow continuous paper flow. | 1 | 353
108 | Loring Elementary School | C. Lavatory (Children) | A. Toe or knee clearances not provided | Boys' Toilet Room | 1 | 167 | Priority 1 | Program Access | Provide at least one lavatory with 25" min. knee clearance positioned for a forward approach. Ensure toe clearance is also provided. | 1 | 1686
109 | Loring Elementary School | C. Lavatory (Children) | A. Toe or knee clearances not provided | Boys' Toilet Room | 2 | 241 | Priority 1 | Program Access | Provide at least one lavatory with 25" min. knee clearance positioned for a forward approach. Ensure toe clearance is also provided. | 1 | 1686
110 | Loring Elementary School | C. Lavatory (Children) | A. Toe or knee clearances not provided | Girls' Toilet Room | 2 | 226 | Priority 1 | Program Access | Provide at least one lavatory with 25" min. knee clearance positioned for a forward approach. Ensure toe clearance is also provided. | 1 | 1686
111 | Loring Elementary School | C. Lavatory (Children) | A. Toe or knee clearances not provided | Girls' Room | 1 | N/A | Priority 1 | Program Access | Provide at least one lavatory with 25" min. knee clearance positioned for a forward approach. Ensure toe clearance is also provided. | 1 | 1686
112 | Loring Elementary School | C. Lavatory (Children) | A. Toe or knee clearances not provided | Boys' Toilet Room | 1 | 147 | Priority 1 | Program Access | Provide at least one lavatory with 25" min. knee clearance positioned for a forward approach. Ensure toe clearance is also provided. | 1 | 1686
113 | Loring Elementary School | C. Lavatory (Children) | A. Toe or knee clearances not provided | Girls' Toilet Room | 1 | 146 | Priority 1 | Program Access | Provide at least one lavatory with 25" min. knee clearance positioned for a forward approach. Ensure toe clearance is also provided. | 1 | 1686
114 | Loring Elementary School | C. Lavatory (Children) | A. Toe or knee clearances not provided E. Exposed plumbing underneath |  | 1 | 109 | Priority 1 | Safety | Provide at least one lavatory with 25" min. knee clearance positioned for a forward approach. Ensure toe clearance is also provided. Insulate or otherwise configure pipes to prevent contact, for at least one lavatory. | 1 | 1778
115 | Loring Elementary School | C. Lavatory (Children) | A. Toe or knee clearances not provided E. Exposed plumbing underneath | Girls' Toilet Room | 1 | 168 | Priority 1 | Safety | Provide at least one lavatory with 25" min. knee clearance positioned for a forward approach. Ensure toe clearance is also provided. Insulate or otherwise configure pipes to prevent contact, for at least one lavatory. | 1 | 1778
116 | Loring Elementary School | C. Lavatory (Children) | A. Toe or knee clearances not provided E. Exposed plumbing underneath | Kindergarten Single-User Toilet Room | 1 | 135 | Priority 1 | Safety | Provide at least one lavatory with 25" min. knee clearance positioned for a forward approach. Ensure toe clearance is also provided. Insulate or otherwise configure pipes to prevent contact, for at least one lavatory. | 1 | 1778
117 | Loring Elementary School | C. Lavatory (Children) | E. Exposed plumbing underneath | Girls' Toilet Room | 1 | 146 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact, for at least one lavatory. | 1 | 92
118 | Loring Elementary School | C. Lavatory (Children) | E. Exposed plumbing underneath | Men's Room | 1 | 127 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact, for at least one lavatory. | 1 | 92
119 | Loring Elementary School | D. Dispensers (Children) | D. Dispenser is a protruding object | Girls' Toilet Room | 1 | 168 | Priority 3 | Additional Access | Relocate dispenser out of the circulation path or place a cane-detectable barrier under the dispenser. | 1 | 306
120 | Loring Elementary School | D. Dispensers (Children) | D. Dispenser is a protruding object | Boys' Toilet Room | 1 | 147 | Priority 3 | Additional Access | Relocate paper towel dispenser out of the circulation path or place a cane-detectable barrier under the dispenser. | 1 | 306
121 | Loring Elementary School | D. Dispensers (Children) | D. Dispenser is a protruding object | Girls' Toilet Room | 1 | 146 | Priority 3 | Additional Access | Relocate dispenser out of the circulation path or place a cane-detectable barrier under the dispenser. | 1 | 306
122 | Loring Elementary School | E. Urinal (Children) | A. Rim > 15" high (MAAB) | Boys' Toilet Room | 2 | 241 | Priority 1 | Program Access | Provide at least one urinal with the rim no higher than 15" above the finished floor. | 1 | 3248
123 | Loring Elementary School | A. Drinking Fountains | H. No drinking fountain provided for standing users | Drinking Fountain | 1 | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users or install a Hi-Lo drinking fountain. | 1 | 4028
124 | Loring Elementary School | A. Drinking Fountains | H. No drinking fountain provided for standing users | Hallway | 1 | 147 | Priority 1 | Program Access | Provide an additional drinking fountain for standing users or install a Hi-Lo drinking fountain. | 1 | 4028
125 | Loring Elementary School | A. Drinking Fountains | H. No drinking fountain provided for standing users | Drinking Fountain | 2 | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users or install a Hi-Lo drinking fountain. | 1 | 4028
126 | Loring Elementary School | B. Sink | A. Clear floor space not provided at sink | Health Exam Room | 1 | 108 | Priority 3 | Additional Access | Provide a 30" by 48" clear floor space positioned for a forward approach. (Relocate stored objects.) | 1 | 0
126 | Loring Elementary School | B. Sink | E. Exposed plumbing underneath sink | Health Exam Room | 1 | 108 | Priority 1 | Safety | Insulate or otherwise configure pipes at sink. | 1 | 92
127 | Loring Elementary School | B. Sink | B. Toe and knee clearances not provided | Learning Center | 1 | 115 | Priority 1 | Program Access | Ensure there is a 27" knee clearance positioned for a forward approach. | 1 | 1686
128 | Loring Elementary School | B. Sink | B. Toe and knee clearances not provided | Grade 4 Classroom | 2 | 216 | Priority 1 | Program Access | Ensure there is a 25" knee clearance positioned for a forward approach. | 1 | 1686
129 | Loring Elementary School | B. Sink | B. Toe and knee clearances not provided E. Exposed plumbing underneath sink | Music Room | 1 | 164 | Priority 1 | Safety | Ensure there is a 27" knee clearance positioned for a forward approach. Insulate or otherwise configure pipes at sink. | 1 | 1778
130 | Loring Elementary School | B. Sink | B. Toe and knee clearances not provided E. Exposed plumbing underneath sink | Work Room | 1 | N/A | Priority 1 | Safety | Ensure there is a 27" knee clearance positioned for a forward approach. Insulate or otherwise configure pipes at sink. | 1 | 1778
131 | Loring Elementary School | B. Sink | B. Toe and knee clearances not provided E. Exposed plumbing underneath sink | Grade 3 Classroom | 2 | 236 | Priority 1 | Safety | Ensure there is a 27" knee clearance positioned for a forward approach. Insulate or otherwise configure pipes at sink. | 1 | 1778
132 | Loring Elementary School | B. Sink | B. Toe and knee clearances not provided E. Exposed plumbing underneath sink | Grade 2 Classroom | 2 | 233 | Priority 1 | Safety | Ensure there is a 27" knee clearance positioned for a forward approach. Insulate or otherwise configure pipes at sink. | 1 | 1778
133 | Loring Elementary School | B. Sink | E. Exposed plumbing underneath sink | Cafetorium | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes at sink. | 1 | 92
134 | Loring Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Grade 1 Classroom | 1 | 162 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact, for at least one sink. Provide at least one sink with 25" high knee and toe clearance positioned for a forward approach. | 1 | 1778
135 | Loring Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Literacy | 1 | 161 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact, for at least one sink. Provide at least one sink with 25" high knee and toe clearance positioned for a forward approach. | 1 | 1778
136 | Loring Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Special Education | 1 | 159 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact, for at least one sink. Provide at least one sink with 25" high knee and toe clearance positioned for a forward approach. | 1 | 1778
137 | Loring Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Kindergarten | 1 | 135 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact, for at least one sink. Provide at least one sink with 25" high knee and toe clearance positioned for a forward approach. | 1 | 1778
138 | Loring Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Spanish | 1 | 133 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact, for at least one sink. Provide at least one sink with 25" high knee and toe clearance positioned for a forward approach. | 1 | 1778
139 | Loring Elementary School | C. Sinks for Children's Use | D. Knee or toe clearance not provided | Grade 5 Classroom | 2 | 220 | Priority 1 | Program Access | Provide at least one sink with 25" high knee and toe clearance positioned for a forward approach. | 1 | 1686
140 | Loring Elementary School | B. Play Areas | A. Accessible route not provided to playground | Entry - Lower Playground Border at Street | Exterior | N/A | Priority 1 | Program Access | Install an accessible route to the playground. Reduce change in level at the playground border to 1/2" max. beveled for a width of 4' wide min. Note: Costs are not included in this catalog because IHCD has been told that Sudbury has budgeted for a new compliant lower playground. | 1 | 0
141 | Loring Elementary School | B. Play Areas | A. Accessible route not provided to playground | Route Between Upper and Lower Outdoor Amenities | Exterior | N/A | Priority 1 | Program Access | Note: An accessible route is not provided from the school basketball court and upper playground to the lower playground area. See Figure 1 in the report narrative for details regarding the relocation of the basketball court and the provision of an accessible route between outdoor amenities. | 1 | 0
142 | Loring Elementary School | B. Play Areas | B. Accessible route not provided around playground | Lower Playground | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route around the play area. Note: Costs are not included in this catalog for an accessible route around the lower playground because IHCD has been told that Sudbury has budgeted for a new compliant lower playground. | 1 | 0
143 | Loring Elementary School | B. Play Areas | B. Accessible route not provided around playground | Upper Playground | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route around the play area. Note: IHCD has been told that Sudbury is relocating the basketball court to the lower outdoor amenities area. (Cost estimate for a 4' wide min. by 150' stone dust path around the perimeter sides of the playground not bordered by the fence.) | 1 | 4800
144 | Loring Elementary School | B. Play Areas | C. Accessible route not provided to play components | Upper Playground | Exterior | N/A | Priority 1 | Program Access | Provide a compliant impact-attenuating surface to and around the play components. (Cost estimate for 1,200 sq. ft. of poured-in-place rubber surface.) | 1 | 16800
145 | Loring Elementary School | B. Play Areas | C. Accessible route not provided to play components | Lower Playground | Exterior | N/A | Priority 1 | Program Access | Provide a compliant impact-attenuating surface to and around the play components. (Cost estimate for 1500 sq. ft. of poured-in-place rubber surface.) Note: Costs for this remedy are not included in this catalog because IHCD has been told that Sudbury has budgeted for a new compliant lower playground. | 1 | 0
146 | Loring Elementary School | C. Field | A. Accessible spaces not provided at team seating C. Field not connected to an accessible route | Baseball Field | Exterior | N/A | Priority 1 | Program Access | Provide a 36" x 48" clear floor space at team seating. Provide an accessible route to the field. (Cost estimate for a 4' wide min. x 240' long stone dust path providing an accessible route to the boundary of sport activity at the baseball field and connecting to the team seating.) | 1 | 7680
147 | Loring Elementary School | D. Court | B. Accessible spaces are not provided at sidelines seating | Gymnasium | 1 | 154 | Priority 1 | Program Access | Provide a 36" x 48" clear floor space at sidelines seating. Number of accessible seats required is based on the total number of bleacher seats. See the 2010 ADA Standards for Accessible Design Table 221.2.1. | 1 | 0
148 | Loring Elementary School | Bench | N/A | Courtyard | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a 36"x48" stable, firm and slip resistant surface at the end of at least one bench in this area so someone using a wheeled mobility device can sit at the end of the bench with shoulder alignment with someone seated on the bench. Suggest asphalt or stone dust as the surface. | 1 | 0
149 | Loring Elementary School | Sign with International Symbol of Accessibility (ISA) | N/A | Accessible Parking Opposite Exit 11 and 10 | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend replacing or repainting the signs with the International Symbol of Accessibility to increase contrast between text and symbols and background and improve legibility of accessible parking signs. | 2 | 0
1 | Nixon Elementary School | A. Exterior Access Route | E. Obstructed by protruding objects | Path to Basketball Court From Back Entrance | Exterior | N/A | Priority 3 | Additional Access | Trim low hanging branches in trees. | 1 | 200
2 | Nixon Elementary School | A. Exterior Access Route | F. Surface openings > 1/2" J. Level changes > 1/4" K. Surface is not stable, firm, and slip-resistant | Back Road From Playground to Front Parking | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. Repair surface. (Cost estimate for a 188' long, 4' wide stone dust route.) | 1 | 6016
3 | Nixon Elementary School | A. Exterior Access Route | F. Surface openings > 1/2" M. Route not maintained in operable working condition | Path to Basketball Court From Back Entrance | Exterior | N/A | Priority 1 | Program Access | Repair asphalt so that openings are 1/2" max. Ensure the accessible route is maintained in operable working condition. (Cost estimate for 6' long by 4' wide area of asphalt.) | 1 | 240
4 | Nixon Elementary School | A. Exterior Access Route | J. Level changes > 1/4" | Egress Door 7 | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. | 1 | 160
5 | Nixon Elementary School | A. Exterior Access Route | K. Surface is not stable, firm, and slip-resistant M. Route not maintained in operable working condition | Path to Football Field and New Playground | Exterior | N/A | Priority 1 | Program Access | Repair surface. Ensure the accessible route is maintained in operable working condition. (Cost estimate for 30' long 4' wide of asphalt.) | 1 | 1200
6 | Nixon Elementary School | A. Exterior Access Route | K. Surface is not stable, firm, and slip-resistant M. Route not maintained in operable working condition | Path to Basketball Court From Back Entrance | Exterior | N/A | Priority 1 | Program Access | Repair surface. Ensure the accessible route is maintained in operable working condition. (Cost estimate for 10' long by 4' wide area of asphalt.) | 1 | 400
7 | Nixon Elementary School | A. Exterior Access Route | K. Surface is not stable, firm, and slip-resistant M. Route not maintained in operable working condition | Path to Basketball Court From Back Entrance | Exterior | N/A | Priority 1 | Program Access | Repair surface. Ensure the accessible route is maintained in operable working condition. (Cost estimate for 10' long by 4' wide area of asphalt.) | 1 | 400
8 | Nixon Elementary School | A. Exterior Access Route | M. Route not maintained in operable working condition | Corridor Exit 12 by Office 19 | 1 | 19 | Priority 1 | Program Access | Ensure the accessible route is maintained in operable working condition. (Cost estimate for 4' x 4' asphalt area.) | 1 | 160
9 | Nixon Elementary School | A. Exterior Access Route | M. Route not maintained in operable working condition | Courtyard Patio | Exterior | N/A | Priority 1 | Program Access | Ensure the accessible route is maintained in operable working condition. | 1 | 0
10 | Nixon Elementary School | A. Exterior Access Route | M. Route not maintained in operable working condition | Egress Door 13 Route | Exterior | N/A | Priority 1 | Program Access | Ensure the accessible route is maintained in operable working condition. | 1 | 160
11 | Nixon Elementary School | A. Exterior Access Route | M. Route not maintained in operable working condition K. Surface is not stable, firm, and slip-resistant | Path to Soccer Field and New Playground | Exterior | N/A | Priority 1 | Program Access | Repair surface. Ensure the accessible route is maintained in operable working condition. (Cost estimate for 10' long 4' wide of asphalt.) | 1 | 400
12 | Nixon Elementary School | A. Exterior Access Route | M. Route not maintained in operable working condition K. Surface is not stable, firm, and slip-resistant | Path to Basketball Court From Back Entrance | Exterior | N/A | Priority 1 | Program Access | Repair surface. Ensure the accessible route is maintained in operable working condition. (Cost estimate for 6' long by 4' wide area of asphalt.) | 1 | 240
13 | Nixon Elementary School | A. Exterior Access Route | N. Accessible route not provided | Courtyard Garden Beds and Bench | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided to the garden beds and one bench in the courtyard. (Cost estimate for a 83' long by 4' wide stone dust walkway.) | 1 | 2656
14 | Nixon Elementary School | A. Exterior Access Route | N. Accessible route not provided | Courtyard Chess Table | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the chess board. (Cost estimate for a 10' long by 4' wide stone dust walkway.) | 1 | 320
15 | Nixon Elementary School | A. Exterior Access Route | N. Accessible route not provided | Bike Rack on Left Side of Entrance | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided. (Cost based on a 6' long by 4' wide stone dust route.) | 1 | 192
16 | Nixon Elementary School | C. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces C. Total # of designated van accessible spaces O. Sign does not have the designation "Van Accessible" | Back Parking Lot | Exterior | N/A | Priority 1 | Program Access | Add the designation "Van Accessible" to one parking space. | 1 | 500
17 | Nixon Elementary School | C. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces C. Total # of designated van accessible spaces O. Sign does not have the designation "Van Accessible" | Front Parking Lot | Exterior | N/A | Priority 1 | Program Access | Add the designation "Van Accessible" to one of the accessible parking spaces. | 1 | 500
18 | Nixon Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided | Egress Door 6 | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. | 1 | 464
19 | Nixon Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Main Entrance Door 1 (Egress) | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
20 | Nixon Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Egress Door 7 | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
21 | Nixon Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Egress Door 2 | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
22 | Nixon Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Egress Door 13 | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
23 | Nixon Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Egress Door 8 | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
24 | Nixon Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Gym Egress Door 9 | 1 | 16 | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
25 | Nixon Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Gym Egress Door 10 | 1 | 16 | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
26 | Nixon Elementary School | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Corridor Exit 12 by Office 19 | 1 | 19 | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
27 | Nixon Elementary School | H. Emergency Exit | R. Door requires > 15 lbs. of force to open | Corridor Exit 12 by Office 19 | 1 | 19 | Priority 3 | Additional Access | Adjust closers of exterior doors so doors do not require more than 15 pounds of force. | 1 | 0
28 | Nixon Elementary School | H. Emergency Exit | R. Door requires > 15 lbs. of force to open | Egress Door 8 | Exterior | N/A | Priority 3 | Additional Access | Adjust closers of exterior doors so doors do not require more than 15 pounds of force. | 1 | 0
29 | Nixon Elementary School | B. Interior Access Route | A. Route < 36" wide | Library Media Center | 1 | 1 | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. | 1 | 0
30 | Nixon Elementary School | B. Interior Access Route | B. Obstructed by protruding objects | Tray Drop by Kitchen Area | 1 | N/A | Priority 3 | Additional Access | Provide a cane-detectable barrier at each side of the tray drop. | 2 | 612
31 | Nixon Elementary School | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Library Media Center | 1 | 1 | Priority 3 | Additional Access | Secure the mat. | 1 | 0
32 | Nixon Elementary School | B. Interior Access Route | F. Surface not stable, firm, and slip-resistant | Spanish Class | 1 | 14 | Priority 3 | Additional Access | Secure the mat. | 1 | 0
33 | Nixon Elementary School | C. Doors, Doorways, & Gates | A. Clear width at door < 32" | Office | 1 | 20 | Priority 3 | Additional Access | Relocate furniture to ensure there is a 32" min wide route into the room. | 1 | 0
34 | Nixon Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Learning Studio | 1 | 22 | Priority 3 | Additional Access | Relocate the table out of the door maneuvering clearance. | 1 | 0
35 | Nixon Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Grade 3 Classroom | 1 | 25 | Priority 3 | Additional Access | Relocate blue storage cart. | 1 | 0
36 | Nixon Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Grade 1 Classroom | 1 | 27 | Priority 3 | Additional Access | Relocate trash bin. | 1 | 0
37 | Nixon Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Counselor's Office | 1 | 35 | Priority 3 | Additional Access | Relocate fire extinguisher out of door maneuvering clearance. | 1 | 0
38 | Nixon Elementary School | D. Ramps | E. Handrails not provided at both sides if rise is > 6" | Accessible Stage Access | 1 | N/A | Priority 3 | Additional Access | Provide handrails on both sides. | 1 | 2640
39 | Nixon Elementary School | H. Signage | C. Raised characters < 48" or > 60" above ground | Gym | 1 | 16 | Priority 2 | Navigational Issue | Mount signs so that the baseline of the lowest tactile character is 48” min. above finished floor and the baseline of the highest tactile character is 60” max. above the finished floor. | 1 | 0
40 | Nixon Elementary School | H. Signage | G. Sign not located on the latch side of the door | Cafeteria | 1 | N/A | Priority 2 | Navigational Issue | Locate sign at permanent rooms alongside the door on the latch side. | 1 | 0
41 | Nixon Elementary School | H. Signage | G. Sign not located on the latch side of the door | Girls' Toilet Room Near the Gym | 1 | N/A | Priority 2 | Navigational Issue | Locate sign at permanent rooms alongside the door on the latch side. | 1 | 0
42 | Nixon Elementary School | J. Service Counter | B. Counter > 36" high | Reception | 1 | N/A | Priority 3 | Additional Access | Provide a counter that is 36" max. above the finished floor. | 1 | 880
43 | Nixon Elementary School | K. Operable Parts | A. Element not on an accessible route H. Not operable with a closed fist | Book Sharing Box | Exterior | N/A | Priority 1 | Program Access | Ensure the library box is located on an accessible route. Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. (Cost estimate for a 6' long by 4' wide stone dust route.) | 1 | 442
44 | Nixon Elementary School | K. Operable Parts | E. Forward reach if obstruction > 20"- 25" deep is > 44" high | Learning Studio | 1 | 22 | Priority 3 | Additional Access | Ensure that the controls for the paper towel dispenser and the soap dispenser are not higher than 44" above the finished floor. | 2 | 512
45 | Nixon Elementary School | K. Operable Parts | F. Side reach if obstruction > 24" deep is > 46" high | Math and Literacy | 1 | 28 | Priority 3 | Additional Access | Ensure that control of the paper towel dispenser is not located any deeper than 24" and any higher than 46" above the finished floor. Relocate file cabinet. | 1 | 256
46 | Nixon Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Library Media Center Computer Terminal | 1 | 1 | Priority 1 | Program Access | Provide at least 1 work surface with 24" min. high knee and toe clearance that has 30" min. clear width. | 1 | 200
47 | Nixon Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Grade 4 Classroom | 1 | 12 | Priority 1 | Program Access | Provide at least 1 work surface with 24" min. high knee and toe clearance that has 30" min. clear width. | 1 | 200
48 | Nixon Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Grade 3 Classroom | 1 | 25 | Priority 1 | Program Access | Provide at least 1 work surface with 24" min. high knee and toe clearance that has 30" min. clear width. | 1 | 200
49 | Nixon Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Grade 2 Classroom | 1 | 26 | Priority 1 | Program Access | Provide at least 1 work surface with 24" min. high knee and toe clearance that has 30" min. clear width. | 1 | 200
50 | Nixon Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Grade 1 Classroom | 1 | 27 | Priority 1 | Program Access | Provide at least 1 work surface with 24" min. high knee and toe clearance that has 30" min. clear width. | 1 | 200
51 | Nixon Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Special Room | 1 | 31 | Priority 1 | Program Access | Provide at least 1 work surface with 24" min. high knee and toe clearance that has 30" min. clear width. | 1 | 200
52 | Nixon Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Special Room | 1 | 33 | Priority 1 | Program Access | Provide at least 1 work surface with 24" min. high knee and toe clearance that has 30" min. clear width. | 1 | 200
53 | Nixon Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Grade 5 Classroom | 1 | 8 | Priority 1 | Program Access | Provide at least 1 work surface with 24" min. high knee and toe clearance that has 30" min. clear width. | 1 | 200
54 | Nixon Elementary School | N. Assembly Area | C. Minimum # wheelchair spaces not provided | Music Room | 1 | 18 | Priority 1 | Program Access | Provide integrated wheelchair spaces in the bleachers based on ADA 2010 Standards 221.2.1.1. | 1 | 0
55 | Nixon Elementary School | N. Assembly Area | P. Assistive listening devices not provided | Special Room | 1 | 33 | Priority 1 | Program Access | If audible communication is integral to the use of the space, provide an assistive listening system. | 1 | 1214
56 | Nixon Elementary School | S. Picnic Tables | G. Toe or knee clearance at tables not provided H. Picnic table not on an accessible route | Courtyard Picnic Area | Exterior | N/A | Priority 1 | Program Access | Provide at least one picnic table has toe and knee clearance. Ensure that the picnic table is connected to an accessible route. (Cost estimate for a 50' long by 4' wide stone dust route and an accessible picnic table.) | 1 | 3000
57 | Nixon Elementary School | S. Picnic Tables | G. Toe or knee clearance at tables not provided H. Picnic table not on an accessible route | Picnic Tables by New Playground | Exterior | N/A | Priority 1 | Program Access | Provide one accessible picnic table in this area and provide an accessible route to it. (Cost estimate for an accessible picnic table and a 30' long by 4' wide asphalt route to it). | 1 | 2600
58 | Nixon Elementary School | S. Picnic Tables | H. Picnic table not on an accessible route | Chess Picnic Table by the New Playground | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to one picnic table in this area. (Cost estimate for a 6' long by 4' wide asphalt route.) | 1 | 240
59 | Nixon Elementary School | T. Exterior Benches | A. No accessible route to one bench in area | Soccer Field Bench | Exterior | N/A | Priority 1 | Program Access | Locate one bench in this area on an accessible route. | 1 | 0
60 | Nixon Elementary School | T. Exterior Benches | A. No accessible route to one bench in area | Bench by the New Playground | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to one bench in this area. (Cost estimate for a 30' long, 4' wide asphalt route.) | 1 | 1200
61 | Nixon Elementary School | T. Exterior Benches | A. No accessible route to one bench in area | Benches in Front of Cafeteria | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to one bench. (Cost estimate for a 6' long 4' wide stone dust walkway.) | 1 | 192
62 | Nixon Elementary School | A. Overall Access | G. 6 fixtures, but no ambulatory compartment provided | Girls' Toilet Room by Room 27 | 1 | N/A | Priority 1 | Program Access | Provide one ambulatory accessible compartment. | 1 | 3012
63 | Nixon Elementary School | A. Overall Access | G. 6 fixtures, but no ambulatory compartment provided | Girls' Toilet Room by the Gym | 1 | N/A | Priority 1 | Program Access | Provide one ambulatory accessible compartment. | 1 | 3012
64 | Nixon Elementary School | A. Overall Access | G. 6 fixtures, but no ambulatory compartment provided | Girls' Toilet Room Near Classroom 8 | 1 | N/A | Priority 1 | Program Access | Provide one ambulatory accessible compartment. | 1 | 3012
65 | Nixon Elementary School | B. Lavatory | B. Toe or knee clearances not provided E. Plumbing underneath is exposed | Health Office Toilet Room | 1 | N/A | Priority 1 | Program Access | Provide at least one lavatory with 27" knee and toe clearance positioned for a forward approach. Insulate or otherwise configure pipes to prevent contact at lavatory. | 1 | 1778
66 | Nixon Elementary School | B. Lavatory | E. Plumbing underneath is exposed | Girls' and Boys' Toilet Rooms by the Gym | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact for at least one lavatory at the high lavatory. | 2 | 184
67 | Nixon Elementary School | B. Lavatory | E. Plumbing underneath is exposed | Boys' Toilet Room Near Classroom 8 | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact for at least one lavatory (the high lavatory). | 1 | 92
68 | Nixon Elementary School | B. Lavatory | E. Plumbing underneath is exposed | Girls' Toilet Room Near Classroom 8 | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact for at least one lavatory (the high lavatory). | 1 | 92
69 | Nixon Elementary School | C. Single-User Toilet | D. Centerline < or > 18" (MAAB) G. Side or rear grab bar < 33" or > 36" high M. Toilet paper dispenser is not compliant | Health Office Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate toilet so that the centerline is 18" from the side wall. Mount grab bars 33"- 36" above the floor. Relocate toilet paper so that it is 24" min. high, located under the grab bar, and between 7" and 9" from the front of the toilet. Ensure it is not mounted over the grab bars. | 1 | 3973
70 | Nixon Elementary School | D. Toilet Compartment | C. Door has non-compliant hardware D. Door has malfunctioning self-closing hinge | Girls' Toilet Room by the Gym | 1 | N/A | Priority 3 | Additional Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. Repair hinge. | 1 | 70
71 | Nixon Elementary School | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Boys' Toilet Room by the Gym | 1 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
72 | Nixon Elementary School | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Girls' Toilet Room Near Classroom 8 | 1 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
73 | Nixon Elementary School | D. Toilet Compartment | D. Door has malfunctioning self-closing hinge | Boys' Toilet Room Near Classroom 8 | 1 | N/A | Priority 3 | Additional Access | Repair hinge. | 1 | 0
74 | Nixon Elementary School | D. Toilet Compartment | M. Flush control not on open side | Girls' Toilet Room Near Classroom 8 | 1 | N/A | Priority 3 | Additional Access | Provide the flush control on the open side of the toilet (transfer side). | 1 | 374
75 | Nixon Elementary School | D. Toilet Compartment | M. Flush control not on open side N. Non-compliant toilet paper dispenser | Girls' Toilet Room by the Gym | 1 | N/A | Priority 3 | Additional Access | Provide the flush control on the open side of the toilet (transfer side). Relocate toilet paper so that it is 24" min. high, located under the grab bar, and between 7" and 9" from the front of the toilet. | 1 | 630
76 | Nixon Elementary School | D. Toilet Compartment | N. Non-compliant toilet paper dispenser | Boys' Toilet Room by the Gym | 1 | N/A | Priority 3 | Additional Access | Relocate toilet paper so that it is 24" min. high, located under the grab bar, and between 7" and 9" from the front of the toilet. | 1 | 256
77 | Nixon Elementary School | F. Dispensers | A. Controls > 42" high D. Dispenser acts as a protruding object | Health Office | 1 | N/A | Priority 3 | Additional Access | Relocate paper towel dispenser so the operable part is 42" max. above the finished floor. Relocate dispenser out of the circulation path. | 1 | 256
78 | Nixon Elementary School | F. Dispensers | D. Dispenser acts as a protruding object | Boys' and Girls' Toilet Rooms by Room 27 | 1 | N/A | Priority 3 | Additional Access | Relocate paper towel dispensers out of the circulation path. | 4 | 1412
79 | Nixon Elementary School | F. Dispensers | D. Dispenser acts as a protruding object | Girls' Toilet Room Near Classroom 8 | 1 | N/A | Priority 3 | Additional Access | Relocate higher paper towel dispenser out of the circulation path. Alternatively, lower it so that the bottom edge is at 27" max. | 1 | 256
80 | Nixon Elementary School | F. Dispensers | D. Dispenser acts as a protruding object | Boys' Toilet Room Near Classroom 8 | 1 | N/A | Priority 3 | Additional Access | Relocate dispensers out of the circulation path. Alternatively, lower them so that the bottom edge is at 27" max. | 2 | 512
81 | Nixon Elementary School | A. Single-User Toilet (Children) | F. Toilet seat < 12" or > 15" high (K - 3) L. Side or rear grab bar < 42" long Q. Non-compliant toilet paper dispenser | Kindergarten Toilet Room | 1 | N/A | Priority 3 | Additional Access | Install a toilet with a seat between 12"- 15" high above the finished floor. Provide a rear wall grab bar that is 42" long located 6" max. from the interior corner. Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars. | 1 | 3417
82 | Nixon Elementary School | B. Toilet Compartment (Children) | B. Door with non-compliant hardware U. Coat hook not within reach range | Boys' Toilet Room by Room 27 | 1 | N/A | Priority 3 | Additional Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. Lower hook so that it is no higher than 44" for children ages 9-12. | 1 | 220
83 | Nixon Elementary School | B. Toilet Compartment (Children) | L. Side or rear grab bar < 25" or > 27" high (Ages 9 - 12) R. Non-compliant toilet paper dispenser | Boys' Toilet Room by Room 27 | 1 | N/A | Priority 3 | Additional Access | Relocate both grab bars to 25"- 27" above the floor. Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars. | 1 | 768
84 | Nixon Elementary School | B. Toilet Compartment (Children) | R. Non-compliant toilet paper dispenser S. Clearance at toilet < 60" clear width | Girls' Toilet Room by Room 27 | 1 | N/A | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars. Remove desk. | 1 | 353
85 | Nixon Elementary School | C. Lavatory (Children) | A. Toe or knee clearances not provided E. Exposed plumbing underneath | Boys' Toilet Room by Room 27 | 1 | N/A | Priority 1 | Safety | Provide at least one lavatory with 25" min. knee clearance positioned for a forward approach. Ensure toe clearance is also provided. Insulate or otherwise configure pipes to prevent contact, for at least one lavatory. | 1 | 1778
85 | Nixon Elementary School | C. Lavatory (Children) | F. Mirror above lavatory w/reflective surface > 31" | Boys' Toilet Room by Room 27 | 1 | N/A | Priority 3 | Additional Access | Lower mirror so that the bottom surface is at 31" above finished floor. | 1 | 256
86 | Nixon Elementary School | C. Lavatory (Children) | E. Exposed plumbing underneath | Kindergarten Toilet Room | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at lavatory. | 1 | 92
87 | Nixon Elementary School | C. Lavatory (Children) | E. Exposed plumbing underneath | Girls' Toilet Room by Room 27 | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at lavatory. | 1 | 92
87 | Nixon Elementary School | C. Lavatory (Children) | F. Mirror above lavatory w/reflective surface > 31" | Girls' Toilet Room by Room 27 | 1 | N/A | Priority 3 | Additional Access | Lower mirror so that the bottom surface is at 31" above finished floor. | 1 | 256
88 | Nixon Elementary School | E. Urinal (Children) | A. Rim > 15" high (MAAB) | Boys' Toilet Room by Room 27 | 1 | N/A | Priority 1 | Program Access | Provide at least one urinal with the rim no higher than 15" above the finished floor. | 1 | 3248
89 | Nixon Elementary School | A. Drinking Fountains | H. No drinking fountain provided for standing users | Drinking Fountain Next to Boys' Toilet Room by Room 27 | 1 | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users. | 1 | 4028
90 | Nixon Elementary School | A. Drinking Fountains | H. No drinking fountain provided for standing users | Fountain Next to Gym | 1 | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users. | 1 | 4028
91 | Nixon Elementary School | A. Drinking Fountains | H. No drinking fountain provided for standing users | Drinking Fountain Between Toilet Rooms Near Classroom 8 | 1 | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users. | 1 | 4028
92 | Nixon Elementary School | A. Drinking Fountains | H. No drinking fountain provided for standing users | Fountain Next to Cafeteria | 1 | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users. | 1 | 4028
93 | Nixon Elementary School | A. Drinking Fountains | H. No drinking fountain provided for standing users | Drinking Fountain by Kitchen Area | 1 | N/A | Priority 1 | Program Access | Install a Hi-Lo drinking fountain. | 1 | 4216
94 | Nixon Elementary School | A. Drinking Fountains | H. No drinking fountain provided for standing users | Drinking Fountain at Playground | Exterior | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users. | 1 | 4028
95 | Nixon Elementary School | B. Sink | E. Exposed plumbing underneath sink | Health Office | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes at sink. | 1 | 92
96 | Nixon Elementary School | C. Sinks for Children's Use | B. Non-compliant or malfunctioning faucet | Kindergarten Classroom | 1 | N/A | Priority 3 | Additional Access | Provide a faucet that can be operable with one hand and not require tight grasping, pinching or twisting of the wrist for at least one sink. | 1 | 986
96 | Nixon Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Kindergarten Classroom | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at the sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
97 | Nixon Elementary School | C. Sinks for Children's Use | B. Non-compliant or malfunctioning faucet | Grade 4 Classroom | 1 | 12 | Priority 3 | Additional Access | Provide a faucet that can be operable with one hand and not require tight grasping, pinching or twisting of the wrist for at least one sink. | 1 | 986
97 | Nixon Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Grade 4 Classroom | 1 | 12 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at the sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
98 | Nixon Elementary School | C. Sinks for Children's Use | B. Non-compliant or malfunctioning faucet | Art Room | 1 | 13 | Priority 3 | Additional Access | Provide a faucet that can be operable with one hand and not require tight grasping, pinching or twisting of the wrist for at least one sink. | 1 | 986
98 | Nixon Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Art Room | 1 | 13 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at the sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
99 | Nixon Elementary School | C. Sinks for Children's Use | B. Non-compliant or malfunctioning faucet | Learning Center | 1 | 21 | Priority 3 | Additional Access | Provide a faucet that can be operable with one hand and not require tight grasping, pinching or twisting of the wrist for at least one sink. | 1 | 986
99 | Nixon Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Learning Center | 1 | 21 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at the sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
100 | Nixon Elementary School | C. Sinks for Children's Use | B. Non-compliant or malfunctioning faucet | Learning Studio | 1 | 22 | Priority 3 | Additional Access | Provide a faucet that can be operable with one hand and not require tight grasping, pinching or twisting of the wrist for at least one sink. | 1 | 986
100 | Nixon Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Learning Studio | 1 | 22 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at the sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
101 | Nixon Elementary School | C. Sinks for Children's Use | B. Non-compliant or malfunctioning faucet | Grade 3 Classroom | 1 | 25 | Priority 3 | Additional Access | Provide a faucet that can be operable with one hand and not require tight grasping, pinching or twisting of the wrist for at least one sink. | 1 | 986
101 | Nixon Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Grade 3 Classroom | 1 | 25 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at the sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
102 | Nixon Elementary School | C. Sinks for Children's Use | B. Non-compliant or malfunctioning faucet | Grade 2 Classroom | 1 | 26 | Priority 3 | Additional Access | Provide a faucet that can be operable with one hand and not require tight grasping, pinching or twisting of the wrist for at least one sink. | 1 | 986
102 | Nixon Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Grade 2 Classroom | 1 | 26 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at the sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
103 | Nixon Elementary School | C. Sinks for Children's Use | B. Non-compliant or malfunctioning faucet | Grade 1 Classroom | 1 | 27 | Priority 3 | Additional Access | Provide a faucet that can be operable with one hand and not require tight grasping, pinching or twisting of the wrist for at least one sink. | 1 | 986
103 | Nixon Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Grade 1 Classroom | 1 | 27 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at the sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
104 | Nixon Elementary School | C. Sinks for Children's Use | B. Non-compliant or malfunctioning faucet | Math and Literacy | 1 | 28 | Priority 3 | Additional Access | Provide a faucet that can be operable with one hand and not require tight grasping, pinching or twisting of the wrist for at least one sink. | 1 | 986
104 | Nixon Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Math and Literacy | 1 | 28 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at the sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
105 | Nixon Elementary School | C. Sinks for Children's Use | B. Non-compliant or malfunctioning faucet | Special Room | 1 | 31 | Priority 3 | Additional Access | Provide a faucet that can be operable with one hand and not require tight grasping, pinching or twisting of the wrist for at least one sink. | 1 | 986
105 | Nixon Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Special Room | 1 | 31 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at the sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
106 | Nixon Elementary School | C. Sinks for Children's Use | B. Non-compliant or malfunctioning faucet | Classroom | 1 | 32 | Priority 3 | Additional Access | Provide a faucet that can be operable with one hand and not require tight grasping, pinching or twisting of the wrist for at least one sink. | 1 | 986
106 | Nixon Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Classroom | 1 | 32 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at the sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
107 | Nixon Elementary School | C. Sinks for Children's Use | B. Non-compliant or malfunctioning faucet | Special Room | 1 | 33 | Priority 3 | Additional Access | Provide a faucet that can be operable with one hand and not require tight grasping, pinching or twisting of the wrist for at least one sink. | 1 | 986
107 | Nixon Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Special Room | 1 | 33 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at the sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
108 | Nixon Elementary School | C. Sinks for Children's Use | B. Non-compliant or malfunctioning faucet | Grade 5 Classroom | 1 | 8 | Priority 3 | Additional Access | Provide a faucet that can be operable with one hand and not require tight grasping, pinching or twisting of the wrist for at least one sink. | 1 | 986
108 | Nixon Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Grade 5 Classroom | 1 | 8 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at the sink. Provide at least one sink with 24" high knee and toe clearance positioned for a forward approach. | 1 | 1778
109 | Nixon Elementary School | C. Field | C. Field not connected to an accessible route | Soccer Field | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the field. (Cost estimate for 30' long by 4' wide stone dust walkway.) | 1 | 960
110 | Nixon Elementary School | N/A | N/A | New Playground | Exterior | N/A |  |  | Note: Playground was under construction and could not be surveyed. | 1 | 0
111 | Nixon Elementary School | N/A | N/A | Cafeteria, Accessible Table | 1 | N/A |  |  | This is a good example of a table with knee and toe clearance. | 1 | 0
112 | Nixon Elementary School | N/A | N/A | Stage Steps | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing handrails on each side. | 1 | 0
113 | Nixon Elementary School | N/A | N/A | Principal's Office | 1 | N/A | Priority 4 | Enhanced Usability | Recommend providing signs with raised characters and braille at permanent rooms where no sign is present. | 1 | 0
114 | Nixon Elementary School | N/A | N/A | Playground | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a 10" high solid surface (kickplate) on the push side of the gate. | 1 | 0
115 | Nixon Elementary School | N/A | N/A | Chess Picnic Table by the New Playground | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a 48" wide accessible route around the accessible picnic table. | 1 | 0
116 | Nixon Elementary School | N/A | N/A | Benches in Front of Cafeteria | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a 36" x 48" space alongside one bench positioned so that a person using a wheelchair can sit shoulder to shoulder with someone seated on the bench. Recommend providing a variety of benches, including benches with backs and armrests. | 1 | 0
1 | Peter Noyes Elementary School | A. Exterior Access Route | B. Exterior route < 36" wide | Route From Doors 9, 10, and 11 to East Side of Building | Exterior | N/A | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the accessible route. (Cost based on 3'x20' of asphalt to correct slope.) | 1 | 600
2 | Peter Noyes Elementary School | A. Exterior Access Route | F. Surface openings > 1/2" | Main Entrance | Exterior | N/A | Priority 1 | Program Access | Fill or seal gap at top of stairs. | 1 | 0
3 | Peter Noyes Elementary School | A. Exterior Access Route | F. Surface openings > 1/2" | Path at Doors 10 and 11 | Exterior | N/A | Priority 3 | Additional Access | Repair asphalt. (Cost for a 4'x4' asphalt patch.) | 1 | 160
4 | Peter Noyes Elementary School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | West Walkway to Playground | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). (Cost based on 3'x4' of asphalt to correct slope.) | 1 | 120
5 | Peter Noyes Elementary School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | West Walkway to Playground | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). (Cost based on 3'x4' of asphalt to correct slope.) | 1 | 120
6 | Peter Noyes Elementary School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Route From Doors 9, 10, and 11 to East Side of Building | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). (Cost based on 3'x20' of asphalt to correct slope.) | 1 | 600
7 | Peter Noyes Elementary School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Route From Doors 9, 10, and 11 to East Side of Building | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). (Cost based on 3'x40' of asphalt to correct slope.) | 1 | 1200
8 | Peter Noyes Elementary School | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) H. Running slope > 1:20 (5%) | West Side of School - Curb Ramp Leads to Playground | Exterior | N/A | Priority 1 | Program Access | Reduce cross slope to be no steeper than 1:50 (2.00%). Reduce running slope to be no steeper than 1:20 (5%). (Cost base on 3'x15' of asphalt to correct slope.) | 1 | 450
9 | Peter Noyes Elementary School | A. Exterior Access Route | H. Running slope > 1:20 (5%) | West Side of School - Leads to Playground | Exterior | N/A | Priority 3 | Additional Access | Reduce running slope to be no steeper than 1:20 (5%). (Cost base on 3'x15' of asphalt to correct slope.) | 1 | 450
10 | Peter Noyes Elementary School | A. Exterior Access Route | J. Level changes > 1/4" | Door 10 | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. where door landing meets asphalt walkway. (Cost for a 4'x4' asphalt patch.) | 1 | 160
11 | Peter Noyes Elementary School | A. Exterior Access Route | J. Level changes > 1/4" | Door 9 | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. where door landing meets asphalt walkway. (Cost for a 4'x4' asphalt patch.) | 1 | 160
12 | Peter Noyes Elementary School | A. Exterior Access Route | J. Level changes > 1/4" | Walkway to Playground From Door 7 | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max., repair asphalt. (Cost based on a 4'x4' asphalt patch.) | 1 | 160
13 | Peter Noyes Elementary School | A. Exterior Access Route | N. Accessible route not provided | Route From Doors 9, 10, and 11 to East Side of Building | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided. Repair walkway. (Cost based on 3'x20' of asphalt to correct walkway.) | 1 | 600
14 | Peter Noyes Elementary School | A. Exterior Access Route | N. Accessible route not provided | Southeast Side of Building | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided. (Cost based on new 4' wide min. x 15' long asphalt walkway.) | 1 | 600
15 | Peter Noyes Elementary School | C. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces C. Total # of designated van accessible spaces P. Sign bottom < 60" above finished grade | West Parking Lot | Exterior | N/A | Priority 1 | Program Access | Locate sign with the bottom of the sign 60" above the ground. | 3 | 0
16 | Peter Noyes Elementary School | C. Off-Street Parking Lot or Garage | B. Total # of designated accessible parking spaces C. Total # of designated van accessible spaces | West Parking Lot | Exterior | N/A | Priority 1 | Program Access | Provide one van accessible space 11' wide min. with a marked access aisle 5' wide min. Include a sign with the International Symbol of Accessibility (ISA) and a sign with the word "Van Accessible" at the van accessible space. Provide a car accessible parking space 8' wide min. with a marked access aisle 5' wide min. and a sign with the International Symbol of Accessibility (ISA). | 2 | 3700
17 | Peter Noyes Elementary School | A. Means of Egress | B. Tactile exit sign not provided | Door 11 | 3 | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. | 1 | 232
18 | Peter Noyes Elementary School | A. Means of Egress | B. Tactile exit sign not provided | Door 3 | 3 | 42 | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. | 1 | 232
19 | Peter Noyes Elementary School | A. Means of Egress | B. Tactile exit sign not provided | Cafeteria | 1 | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. | 1 | 232
20 | Peter Noyes Elementary School | A. Means of Egress | B. Tactile exit sign not provided O. Illuminated ISA symbol not provided (MAAB) | Main Entrance | 3 | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
21 | Peter Noyes Elementary School | A. Means of Egress | B. Tactile exit sign not provided O. Illuminated ISA symbol not provided (MAAB) | Door 10 | 3 | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. (Exterior landing is just .75" high and can be patched to make accessible.) | 1 | 432
22 | Peter Noyes Elementary School | A. Means of Egress | B. Tactile exit sign not provided O. Illuminated ISA symbol not provided (MAAB) | Door 7 | 2 | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
23 | Peter Noyes Elementary School | A. Means of Egress | B. Tactile exit sign not provided O. Illuminated ISA symbol not provided (MAAB) | Door 8 | 2 | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 432
24 | Peter Noyes Elementary School | A. Means of Egress | B. Tactile exit sign not provided O. Illuminated ISA symbol not provided (MAAB) | Door 9 | Exterior | N/A | Priority 1 | Safety | Ensure tactile exit signs with raised characters and braille are provided at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. (Exterior landing is just .2" high and can be patched to make accessible.) | 1 | 432
25 | Peter Noyes Elementary School | B. Interior Access Route | B. Obstructed by protruding objects | Cafeteria | 1 | N/A | Priority 3 | Additional Access | Relocate object out of circulation path or provide a cane-detectable barrier. | 1 | 306
26 | Peter Noyes Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Office - Nurse's Room | 3 | N/A | Priority 3 | Additional Access | Remove furniture to provide 18" min. pull-side maneuvering clearance at door. | 1 | 0
27 | Peter Noyes Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | School Psychologist | 3 | N/A | Priority 3 | Additional Access | Remove chair t0 provide maneuvering 18" min. maneuvering clearance at door clearance. | 1 | 0
28 | Peter Noyes Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Shining Stars | 4 | 49 | Priority 3 | Additional Access | Relocate table to provide 18" min. pull-side maneuvering clearance. | 1 | 0
29 | Peter Noyes Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Music Room - Strings | 1 | 51 | Priority 3 | Additional Access | Remove the stored item to provide 18" min. pull-side maneuvering clearance at door. | 1 | 0
30 | Peter Noyes Elementary School | C. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Gender Neutral Toilet Room | 2 | N/A | Priority 3 | Additional Access | Remove desk to provide 18" min. pull side maneuvering clearance at the door. | 1 | 0
31 | Peter Noyes Elementary School | C. Doors, Doorways, & Gates | D. Maneuvering clearance not provided at recess > 6” | Special Education Room | 4 | 7 | Priority 3 | Additional Access | Install an automatic door opener. | 1 | 3060
32 | Peter Noyes Elementary School | C. Doors, Doorways, & Gates | D. Maneuvering clearance not provided at recess > 6” | Learning Center - Grades 3-5 | 4 | 1 | Priority 3 | Additional Access | Install an automatic door opener. | 1 | 3060
33 | Peter Noyes Elementary School | C. Doors, Doorways, & Gates | D. Maneuvering clearance not provided at recess > 6” | Girls' Toilet Room | 1 | N/A | Priority 3 | Additional Access | Install an automatic door opener. | 1 | 3060
34 | Peter Noyes Elementary School | C. Doors, Doorways, & Gates | D. Maneuvering clearance not provided at recess > 6” | Boys' Toilet Room | 1 | N/A | Priority 3 | Additional Access | Install an automatic door opener. | 1 | 3060
35 | Peter Noyes Elementary School | C. Doors, Doorways, & Gates | D. Maneuvering clearance not provided at recess > 6” | Learning Center - Grades K-2 | 4 | 1 | Priority 3 | Additional Access | Install an automatic door opener./Reverse the swing of the door to provide maneuvering clearance. | 1 | 3060
36 | Peter Noyes Elementary School | C. Doors, Doorways, & Gates | H. Mat not securely attached | Library | 3 | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
37 | Peter Noyes Elementary School | C. Doors, Doorways, & Gates | H. Mat not securely attached | Door 7 | 2 | N/A | Priority 3 | Additional Access | Secure the mat. | 1 | 0
38 | Peter Noyes Elementary School | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Occupational Therapy Office | 4 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
39 | Peter Noyes Elementary School | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Learning Center | 4 | 43 | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
40 | Peter Noyes Elementary School | C. Doors, Doorways, & Gates | M. Door requires > 5 lbs. of force to open | Lift to Stage | 3 | 42 | Priority 3 | Additional Access | Adjust closers on lift so doors do not require more than 5 pounds of force to open. | 1 | 0
41 | Peter Noyes Elementary School | H. Signage | A. Signage is not provided | Learning Studio | 3 | 39 | Priority 1 | Program Access | Provide designation signage with the words, "Learning Studio" Current sign says, "Computer Lab" Locate compliant signage alongside the door on the latch side. | 1 | 232
42 | Peter Noyes Elementary School | H. Signage | A. Signage is not provided | Occupational Therapy Office | 4 | N/A | Priority 1 | Program Access | Locate compliant signage with raised characters and braille alongside the door on the latch side. | 1 | 232
43 | Peter Noyes Elementary School | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign | School Psychologist | 3 | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. | 1 | 232
44 | Peter Noyes Elementary School | H. Signage | B. Raised characters not provided on sign D. Braille not provided on sign F. Visual characters < 40" above ground G. Sign not located on the latch side of the door | Grade 5 | 4 | 10 | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille on sign. Provide braille on sign. Mount visual sign so that the baseline of the lowest character is 40" min. above the finished floor. Locate sign at permanent rooms alongside the door on the latch side. | 10 | 2320
45 | Peter Noyes Elementary School | H. Signage | C. Raised characters < 48" or > 60" above ground | Inaccessible Toilet Rooms | 1 | N/A | Priority 2 | Navigational Issue | Mount signs so that the baseline of the lowest tactile character is 48” min. above finished floor and the baseline of the highest tactile character is 60” max. above the finished floor. | 2 | 0
46 | Peter Noyes Elementary School | H. Signage | G. Sign not located on the latch side of the door | Literacy Center | 3 | 34 | Priority 2 | Navigational Issue | Locate sign at permanent rooms alongside the door on the latch side. | 1 | 0
47 | Peter Noyes Elementary School | L. Children's Reach Ranges | D. Reach < 18" or > 40" (Ages 5 - 8) | Learning Studio | 3 | 39 | Priority 3 | Additional Access | Provide at least one storage bin located between 18" and 40" above the finished floor. | 1 | 256
48 | Peter Noyes Elementary School | L. Children's Reach Ranges | D. Reach < 18" or > 40" (Ages 5 - 8) | Hallway - Kindergarten Wing | 3 | N/A | Priority 3 | Additional Access | Provide at least one coat hook for children no higher that 40" above the finished floor. | 1 | 256
49 | Peter Noyes Elementary School | M. Dining or Work Surfaces | B. At least one or 5% accessible tables not provided | Cafeteria | 1 | N/A | Priority 1 | Program Access | Ensure that 5% min. of the 21 dining surfaces in the cafeteria are accessible (have knee and toe clearance). | 3 | 3300
50 | Peter Noyes Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | Guidance Counselor | 3 | N/A | Priority 1 | Program Access | Provide at least 1 dining or work surface with 27" min. knee and toe clearance. (Table feet block toe clearance.) | 1 | 700
51 | Peter Noyes Elementary School | M. Dining or Work Surfaces | C. Knee or toe clearance not provided | School Psychologist | 3 | N/A | Priority 1 | Program Access | Provide at least 1 work surface with 27" min. knee and toe clearance. (Table feet block toe clearance.) | 1 | 700
52 | Peter Noyes Elementary School | M. Dining or Work Surfaces | D. Top of dining/work surface < 28" or > 34" | Library | 3 | N/A | Priority 3 | Additional Access | Provide at least one computer station work surface with tops between 28"- 34" above the floor and 27" clear height underneath. Relocate one computer. | 1 | 0
53 | Peter Noyes Elementary School | Sign | Z. Clear floor space not provided at sign | Office - Future Nurse's Office | 3 | N/A | Priority 3 | Additional Access | Relocate furniture so that there is a clear floor space of 18" min. by 18" min. centered on the tactile characters of the sign. | 1 | 0
54 | Peter Noyes Elementary School | A. Overall Access | E. Sign to accessible toilet not provided | Boys' Toilet Room by Cafeteria | 1 | N/A | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible toilet or bathing room. | 1 | 232
55 | Peter Noyes Elementary School | A. Overall Access | E. Sign to accessible toilet not provided | Girls' Toilet Room by Cafeteria | 1 | N/A | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible toilet or bathing room. | 1 | 232
56 | Peter Noyes Elementary School | A. Overall Access | E. Sign to accessible toilet not provided | Inaccessible Toilet Rooms | 1 | N/A | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible toilet or bathing room. | 2 | 464
57 | Peter Noyes Elementary School | A. Overall Access | E. Sign to accessible toilet not provided | Inaccessible Toilet Rooms | 1 | N/A | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible toilet or bathing room. | 2 | 464
58 | Peter Noyes Elementary School | A. Single-User Toilet (Children) | A. Clearance at toilet < 72" clear deep F. Toilet seat < 12" or > 15" high (K - 3) J. Centerline < 12" or > 15" (K - 3) N. Side or rear grab bar < 20" or > 25" high (K - 3) Q. Non-compliant toilet paper dispenser | Gender Neutral Toilet Room | 2 | N/A | Priority 3 | Additional Access | Renovate toilet room to provide a clear floor space that is 72" deep min. by moving toilet to back wall. Install a toilet with a seat between 12"- 15" high above the finished floor. Relocate toilet so that the centerline is between 12" and 15" from the side wall. Locate grab bar between 20"- 25" above the floor. Relocate toilet paper dispenser so that it is not mounted above grab bars. | 1 | 3973
59 | Peter Noyes Elementary School | A. Single-User Toilet (Children) | B. Clearance at toilet < 60" clear wide | Office - Nurse's Room | 3 | N/A | Priority 3 | Additional Access | Remove desk from transfer clear floor space at toilet. | 1 | 0
60 | Peter Noyes Elementary School | A. Single-User Toilet (Children) | D. Flush control not on open side Q. Non-compliant toilet paper dispenser | Girls' Toilet Room | 3 | N/A | Priority 3 | Additional Access | Move the flush control to the open side. Mount flush control between 20" - 30" above the floor. Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars./Replace dispenser as it does not allow continuous paper flow. | 1 | 727
61 | Peter Noyes Elementary School | A. Single-User Toilet (Children) | P. Side or rear grab bar not provided Q. Non-compliant toilet paper dispenser | Pre-K Classroom | 3 | 25 | Priority 1 | Program Access | Provide one grab bar on the rear wall. Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars./Replace dispenser as it does not allow continuous paper flow. | 1 | 802
62 | Peter Noyes Elementary School | A. Single-User Toilet (Children) | Q. Non-compliant toilet paper dispenser | Office - Nurse's Room | 3 | N/A | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars./Replace dispenser as it does not allow continuous paper flow. | 1 | 353
63 | Peter Noyes Elementary School | B. Toilet Compartment (Children) | F. Toilet seat < 12" or > 15" high (Ages 5 - 8) N. Flush control not on open side P. Centerline < 12" or > 15" (Ages 5 - 8) R. Non-compliant toilet paper dispenser | Boys' Toilet Room | 4 | N/A | Priority 3 | Additional Access | Install a toilet with a seat between 12"- 15" high above the finished floor. Provide the flush control on the open side of the toilet (transfer side), no higher than 44". Relocate toilet so that the centerline is between 12" and 15" from the side wall. Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet below grab bar. | 1 | 3555
64 | Peter Noyes Elementary School | B. Toilet Compartment (Children) | N. Flush control not on open side P. Centerline < 12" or > 15" (Ages 5 - 8) R. Non-compliant toilet paper dispenser | Girls' Toilet Room | 1 | N/A | Priority 3 | Additional Access | Provide the flush control on the open side of the toilet (transfer side), no higher than 44". Relocate toilet so that the centerline is between 12" and 15" from the side wall. Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars. | 1 | 3555
65 | Peter Noyes Elementary School | B. Toilet Compartment (Children) | N. Flush control not on open side R. Non-compliant toilet paper dispenser | Boys' Toilet Room | 2 | N/A | Priority 3 | Additional Access | Provide the flush control on the open side of the toilet (transfer side), no higher than 44". Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars. / Replace dispenser as it does not allow continuous paper flow. | 1 | 727
66 | Peter Noyes Elementary School | B. Toilet Compartment (Children) | P. Centerline < 12" or > 15" (Ages 5 - 8) R. Non-compliant toilet paper dispenser | Girls' Toilet Room | 2 | N/A | Priority 3 | Additional Access | Relocate toilet so that the centerline is between 12" and 15" from the side wall. Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars. | 1 | 3181
67 | Peter Noyes Elementary School | B. Toilet Compartment (Children) | R. Non-compliant toilet paper dispenser | Girls' Toilet Room | 4 | N/A | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars./Replace dispenser as it does not allow continuous paper flow. | 1 | 353
68 | Peter Noyes Elementary School | B. Toilet Compartment (Children) | R. Non-compliant toilet paper dispenser | Boys' Toilet Room | 3 | N/A | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars./Replace dispenser as it does not allow continuous paper flow. | 1 | 353
69 | Peter Noyes Elementary School | B. Toilet Compartment (Children) | R. Non-compliant toilet paper dispenser | Boys' Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate toilet paper dispenser so that it is between 14"- 19" above the floor and between 7"- 9" in front of the toilet. Ensure dispensers and other devices are not mounted above grab bars./Replace dispenser as it does not allow continuous paper flow. | 1 | 353
70 | Peter Noyes Elementary School | C. Lavatory (Children) | A. Toe or knee clearances not provided E. Exposed plumbing underneath | Boys' Toilet Room | 3 | N/A | Priority 1 | Safety | Provide at least one lavatory with 25" min. knee clearance positioned for a forward approach. Ensure toe clearance is also provided. Insulate or otherwise configure pipes to prevent contact, for at least one lavatory. | 1 | 1778
70 | Peter Noyes Elementary School | C. Lavatory (Children) | F. Mirror above lavatory w/reflective surface > 31" | Boys' Toilet Room | 3 | N/A | Priority 3 | Additional Access | Lower mirror so that the bottom surface is at 31" above finished floor. | 1 | 256
71 | Peter Noyes Elementary School | C. Lavatory (Children) | A. Toe or knee clearances not provided E. Exposed plumbing underneath | Girls' Toilet Room | 1 | N/A | Priority 1 | Safety | Provide at least one lavatory with 25" min. knee clearance positioned for a forward approach. Ensure toe clearance is also provided. Insulate or otherwise configure pipes to prevent contact, for at least one lavatory. | 1 | 1778
71 | Peter Noyes Elementary School | C. Lavatory (Children) | F. Mirror above lavatory w/reflective surface > 31" | Girls' Toilet Room | 1 | N/A | Priority 3 | Additional Access | Lower mirror so that the bottom surface is at 31" above finished floor. | 1 | 256
72 | Peter Noyes Elementary School | C. Lavatory (Children) | A. Toe or knee clearances not provided F. Mirror above lavatory w/reflective surface > 31" | Pre-K Classroom | 3 | 25 | Priority 1 | Program Access | Provide at least one lavatory with 25" min. knee clearance positioned for a forward approach. Ensure toe clearance is also provided. Lower mirror so that the bottom surface is at 31" above finished floor. | 1 | 1942
73 | Peter Noyes Elementary School | C. Lavatory (Children) | A. Toe or knee clearances not provided F. Mirror above lavatory w/reflective surface > 31" | Girls' Toilet Room | 4 | N/A | Priority 1 | Program Access | Provide at least one lavatory with 25" min. knee clearance positioned for a forward approach. Ensure toe clearance is also provided. Lower mirror so that the bottom surface is at 31" above finished floor. | 1 | 1942
74 | Peter Noyes Elementary School | C. Lavatory (Children) | A. Toe or knee clearances not provided F. Mirror above lavatory w/reflective surface > 31" | Boys' Toilet Room | 4 | N/A | Priority 1 | Program Access | Provide at least one lavatory with 25" min. knee clearance positioned for a forward approach. Ensure toe clearance is also provided. Lower mirror so that the bottom surface is at 31" above finished floor. | 1 | 1942
75 | Peter Noyes Elementary School | C. Lavatory (Children) | E. Exposed plumbing underneath | Girls' Toilet Room | 3 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact, for at least one lavatory. | 1 | 92
75 | Peter Noyes Elementary School | C. Lavatory (Children) | F. Mirror above lavatory w/reflective surface > 31" | Girls' Toilet Room | 3 | N/A | Priority 3 | Additional Access | Lower mirror so that the bottom surface is at 31" above finished floor. | 1 | 256
76 | Peter Noyes Elementary School | C. Lavatory (Children) | E. Exposed plumbing underneath | Boys' Toilet Room | 3 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact, for at least one lavatory. | 1 | 92
76 | Peter Noyes Elementary School | C. Lavatory (Children) | F. Mirror above lavatory w/reflective surface > 31" | Boys' Toilet Room | 3 | N/A | Priority 3 | Additional Access | Lower mirror so that the bottom surface is at 31" above finished floor. | 1 | 256
77 | Peter Noyes Elementary School | C. Lavatory (Children) | E. Exposed plumbing underneath | Boys' Toilet Room | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact, for at least one lavatory. | 1 | 92
77 | Peter Noyes Elementary School | C. Lavatory (Children) | F. Mirror above lavatory w/reflective surface > 31" | Boys' Toilet Room | 1 | N/A | Priority 3 | Additional Access | Lower mirror so that the bottom surface is at 31" above finished floor. | 1 | 256
78 | Peter Noyes Elementary School | C. Lavatory (Children) | E. Exposed plumbing underneath | Girls' Toilet Room | 3 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact, for at least one lavatory. | 1 | 92
78 | Peter Noyes Elementary School | C. Lavatory (Children) | F. Mirror above lavatory w/reflective surface > 31" | Girls' Toilet Room | 3 | N/A | Priority 3 | Additional Access | Lower mirror so that the bottom surface is at 31" above finished floor. | 1 | 256
79 | Peter Noyes Elementary School | C. Lavatory (Children) | F. Mirror above lavatory w/reflective surface > 31" | Office - Nurse's Room | 3 | N/A | Priority 3 | Additional Access | Lower mirror so that the bottom surface is at 31" above finished floor. | 1 | 256
80 | Peter Noyes Elementary School | D. Dispensers (Children) | A. Dispenser controls > 42" high D. Dispenser is a protruding object | Girls' Toilet Room | 2 | N/A | Priority 3 | Additional Access | Relocate so the operable part of the paper towel dispenser is 42" max. above the finished floor. Relocate dispenser out of the circulation path or provide a cane-detectible-barrier. | 1 | 353
81 | Peter Noyes Elementary School | D. Dispensers (Children) | D. Dispenser is a protruding object | Boys' Toilet Room | 4 | N/A | Priority 3 | Additional Access | Relocate dispenser out of the circulation path or provide a cane-detectible barrier. | 1 | 353
82 | Peter Noyes Elementary School | D. Dispensers (Children) | D. Dispenser is a protruding object | Girls' Toilet Room | 3 | N/A | Priority 3 | Additional Access | Relocate dispenser out of the circulation path or provide a cane-detectible barrier. | 1 | 353
83 | Peter Noyes Elementary School | A. Drinking Fountains | H. No drinking fountain provided for standing users | Near Toilet Rooms | 3 | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users or install a Hi-Lo drinking fountain. | 1 | 4216
84 | Peter Noyes Elementary School | A. Drinking Fountains | H. No drinking fountain provided for standing users | Cafeteria | 1 | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users or install a Hi-Lo drinking fountain. | 1 | 4216
85 | Peter Noyes Elementary School | A. Drinking Fountains | H. No drinking fountain provided for standing users | By Toilet Rooms | 1 | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users or install a Hi-Lo drinking fountain. | 1 | 4216
86 | Peter Noyes Elementary School | A. Drinking Fountains | H. No drinking fountain provided for standing users L. Knee or toe clearance not provided | Near Toilet Rooms | 4 | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users or install a Hi-Lo drinking fountain. Provide knee and toe clearance, 27" min. high at drinking fountain for seated users. (Cost based on a new Hi-Lo drinking fountain.) | 1 | 4216
87 | Peter Noyes Elementary School | A. Drinking Fountains | H. No drinking fountain provided for standing users L. Knee or toe clearance not provided | Near Toilet Rooms | 2 | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users or install a Hi-Lo drinking fountain. Provide knee and toe clearance, 27" min. high at drinking fountain for seated users. (Cost based on a new Hi-Lo drinking fountain.) | 1 | 4216
88 | Peter Noyes Elementary School | A. Drinking Fountains | L. Knee or toe clearance not provided H. No drinking fountain provided for standing users | Hallway to Pre-K Classrooms | 3 | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users or install a Hi-Lo drinking fountain. Provide knee and toe clearance, 27" min. high at drinking fountain for seated users. (Cost based on a new Hi-Lo drinking fountain.) | 1 | 4216
89 | Peter Noyes Elementary School | B. Sink | A. Clear floor space not provided at sink B. Toe and knee clearances not provided | Special Education Room | 4 | 7 | Priority 1 | Program Access | Provide a 30" by 48" clear floor space positioned for a forward approach. Ensure there is a 27" knee clearance positioned for a forward approach. | 1 | 1686
90 | Peter Noyes Elementary School | B. Sink | B. Toe and knee clearances not provided | Learning Studio | 3 | 39 | Priority 1 | Program Access | Ensure there is a 27" knee clearance positioned for a forward approach. | 1 | 1686
91 | Peter Noyes Elementary School | B. Sink | B. Toe and knee clearances not provided | Kindergarten | 3 | 35 | Priority 1 | Program Access | Ensure there is a 27" knee clearance positioned for a forward approach. | 1 | 1686
92 | Peter Noyes Elementary School | B. Sink | B. Toe and knee clearances not provided | Grade 4 | 4 | 8 | Priority 1 | Program Access | Ensure there is a 27" knee clearance positioned for a forward approach. | 1 | 1686
93 | Peter Noyes Elementary School | B. Sink | B. Toe and knee clearances not provided | Learning Center - Grades 3-5 | 4 | 1 | Priority 1 | Program Access | Ensure there is a 27" knee clearance positioned for a forward approach. | 1 | 1686
94 | Peter Noyes Elementary School | B. Sink | B. Toe and knee clearances not provided | Learning Center - Grades K-2 | 4 | 12 | Priority 1 | Program Access | Ensure there is a 27" knee clearance positioned for a forward approach. | 1 | 1686
95 | Peter Noyes Elementary School | B. Sink | B. Toe and knee clearances not provided | Grade 2 | 2 | 22 | Priority 1 | Program Access | Ensure there is a 27" knee clearance positioned for a forward approach. | 1 | 1686
96 | Peter Noyes Elementary School | B. Sink | B. Toe and knee clearances not provided | Grade 1 | 2 | 20 | Priority 1 | Program Access | Ensure there is a 27" knee clearance positioned for a forward approach. | 1 | 1686
97 | Peter Noyes Elementary School | C. Sinks for Children's Use | C. Exposed plumbing underneath D. Knee or toe clearance not provided | Pre-K Classroom | 3 | 25 | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact, for at least one sink. Provide at least one sink with 25" high knee and toe clearance positioned for a forward approach. | 1 | 1778
98 | Peter Noyes Elementary School | B. Play Areas | B. Accessible route not provided around playground | Playground | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route around the perimeter of the play area. (Cost estimate for 4' wide min. x 420' long stone dust path around the perimeter of the playground. See Figure 1 in the report narrative.) | 1 | 13440
99 | Peter Noyes Elementary School | B. Play Areas | C. Accessible route not provided to play components | Playground Element | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the play element. (Cost for a 4' wide min. x 12' long stone dust path from playground to play element. See Figure 1 in the report narrative.) | 1 | 384
100 | Peter Noyes Elementary School | C. Field | A. Accessible spaces not provided at team seating B. Accessible spaces not provided at sidelines seating C. Field not connected to an accessible route | Baseball Field - Northwest of Playground | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the boundary of sport activity at both baseball fields and to player and fan seating at both fields. See Figure 1 in the report narrative.) (Cost based on 420' X' of 4' wide min. of stone dust path connecting elements.) | 1 | 13440
101 | Peter Noyes Elementary School | C. Field | C. Field not connected to an accessible route | Soccer Field - Northwest of Playground | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the boundary of sport activity at the soccer field. (Cost for a 4' wide min. x 30' long stone dust path from playground to play element. Actual cost dependent on where soccer nets are positioned in the field. See Figure 1 in the report narrative.) | 1 | 480
102 | Peter Noyes Elementary School | D. Court | B. Accessible spaces are not provided at sidelines seating | Gymnasium | 3 | 42 | Priority 1 | Program Access | When bleachers are replaced, purchase bleachers with integrated accessible seating. | 1 | 0
103 | Peter Noyes Elementary School | Bench | N/A | Main Entrance | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend a 36"x48" stable, firm and slip resistant space at the end of at least one bench in each area so a companion in a wheeled mobility device can sit alongside someone on the bench. | 1 | 0
104 | Peter Noyes Elementary School | Sandbox Play Area | N/A | Entrance to Playground | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend repositioning sandbox at playground entrance away from accessible route to playground so children playing with the sandbox don't obstruct the accessible route to the playground. | 1 | 0

## Parks
Town of Sudbury: Priority for ADA Transition Plan - Parks | Column1 | Column2 | Column3 | Column4 | Column5 | Column6 | Column7 | Column8 | Column9 | Column10 | Column11 | Column12 | Column13 | Column14
| Priorities: Priority 1: Program Access* or Safety Priority 2: Navigational Issue Priority 3: Additional Access* Priority 4: Enhanced Usability" | *Note: Some toilet rooms issues compromise Program Access. Some toilet rooms with less central issues (e.g., partially accessible toilet rooms), fall under Additional Access. | **IHCD Cost Estimation Notes: - Cost of design is not included. - Does not include costs when note indicates future work. - Labor cannot be estimated for all remedies. - There is no cost noted when it's presumed to be a maintenance issue. - Cost based on a national average. Cost is not based on prevailing wage. - There is no cost noted when it's presumed to be a maintenance issue. Estimates are intended as a guide to budgeting access modifications and are not intended to be absolutely comprehensive or definitive.
| Information Provided by Institute for Human Centered Design | [10 empty] | Project Management for the Town of Sudbury
ID | Facility Name | Element | Issue/Physical Barrier | Location | Floor | Room | Town Priority | Priority for Barrier Removal | Remedies | Quantity | Estimated Cost of Barrier Removal | Project Start Date | Project Completion Date | Responsible for Barrier Removal
1 | Broadacres Farm | A. Exterior Access Route | H. Running slope > 1:20 (5%) K. Surface is not stable, firm, and slip-resistant N. Accessible route not provided | Path Between Horse Riding Practice Building and Horse Barn | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided with a slope no greater than 1:20 (5.00%). (Cost estimate for a 250' long 4' wide stone dust walkway.) | 1 | 8000
2 | Broadacres Farm | A. Exterior Access Route | J. Level changes > 1/4" | House Entrance | Exterior | N/A | Priority 1 | Program Access | Alter change in level to be 1/4" high max. (Cost estimate for a 4' by 4' asphalt area.) | 1 | 160
3 | Broadacres Farm | A. Exterior Access Route | N. Accessible route not provided | Horse Riding Practice Building | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided to the new main entrance door. (Cost estimate for a 10' long 4' wide stone dust walkway.) | 1 | 320
4 | Broadacres Farm | A. Exterior Access Route | N. Accessible route not provided | Kitchen Egress to Outdoor Office | Exterior | N/A | Priority 1 | Program Access | Due to lack of space an accessible route may not be technically feasible to the outdoor office. | 1 | 0
5 | Broadacres Farm | C. Off-Street Parking Lot or Garage | A. Total # of parking C. Total # of designated van accessible spaces | Parking Area | Exterior | N/A | Priority 1 | Program Access | Provide one van accessible parking space. | 1 | 1850
6 | Broadacres Farm | E. Exterior Ramp | A. No lower handrail 18"-20" high provided B. Ramp < 48" wide G. Handrails do not extend 12" past top & bottom H. Handrails have non-compliant cross section Z. Ramp is not located on an accessible route | House - Main Entrance | Exterior | N/A | Priority 3 | Additional Access | Rebuild ramp so that there is 48" inches clear. Provide a lower handrail between 18" to 20" high on each side. Provide handrails that extend horizontally above the landing for 12" min. beyond the top and bottom of ramp runs. Provide handrails with 1-1/4"to 1-1/2" circular cross sections. (Cost estimate for a new 30' pressure treaded wood ramp.). | 1 | 7843
7 | Broadacres Farm | G. Entrance | B. Entrance not on an accessible route C. Directional sign to accessible entrance not provided | Horse Riding Practice Building Inaccessible Door | Exterior | N/A | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible entrance. | 1 | 346
8 | Broadacres Farm | G. Entrance | B. Entrance not on an accessible route O. Threshold > 1/2" high Q. Hardware not operable with a closed fist D. International Symbol of Accessibility not provided | Horse Riding Practice Building Observation Area | Exterior | N/A | Priority 1 | Program Access | After the entrance is made accessible, provide a sign with the International Symbol of Accessibility (ISA). Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. Provide a sloped walkway with a 5' by 5' level platform at the door. (Cost estimate includes a 15' long concrete route to the door, door hardware and sign.) | 1 | 2030
9 | Broadacres Farm | G. Entrance | D. International Symbol of Accessibility not provided | Horse Riding Practice Building Main Entrance | Exterior | N/A | Priority 1 | Program Access | Provide a sign with the International Symbol of Accessibility (ISA) at the new accessible entrance door. | 1 | 346
10 | Broadacres Farm | G. Entrance | O. Threshold > 1/2" high Q. Hardware not operable with a closed fist | House - Main Entrance | Exterior | N/A | Priority 3 | Additional Access | Alter threshold to be 1/2" high max. Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 634
11 | Broadacres Farm | G. Entrance | R. Door requires > 15 lbs. of force to open | Horse Riding Practice Building Main Entrance | Exterior | N/A | Priority 3 | Additional Access | Provide an accessible door into the facility. (Cost estimate for installing a solid core wood door.) | 1 | 2972
12 | Broadacres Farm | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided | Kitchen Egress | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. | 1 | 464
13 | Broadacres Farm | H. Emergency Exit | B. Tactile sign not provided at exit C. Directional sign to accessible emergency exit not provided | Horse Riding Practice Building Inaccessible Door | Exterior | N/A | Priority 2 | Navigational Issue | At the interior of the exit door: provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide a directional sign indicating the location of the nearest accessible emergency exit. | 1 | 464
14 | Broadacres Farm | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Horse Barn Exit | 1 | N/A | Priority 2 | Navigational Issue | Provide tactile exit signs with raised characters and braille at exit doors. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. Provide an illuminated sign with the International Symbol of Accessibility. | 1 | 1116
15 | Broadacres Farm | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | Horse Riding Practice Building Observation Area | Exterior | N/A | Priority 2 | Navigational Issue | Provide a tactile exit signs with raised characters and braille at the interior. Mount signs between 48”- 60” above the finished floor located on the latch side of the door. After the door is made accessible, provide an illuminated sign with the International Symbol of Accessibility on the interior of the door. | 1 | 1116
16 | Broadacres Farm | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) | House - Main Entrance | Exterior | N/A | Priority 2 | Navigational Issue | Provide a tactile exit sign with raised characters and braille at the interior of the exit door. Mount sign between 48”- 60” above the finished floor located on the latch side of the door. After the exit is made accessible, provide an illuminated sign with the International Symbol of Accessibility. | 1 | 1116
17 | Broadacres Farm | H. Emergency Exit | B. Tactile sign not provided at exit D. Illuminated Int. Symbol of Acc. not provided (MAAB) C. Directional sign to accessible emergency exit not provided | Horse Riding Practice Building Main Entrance | Exterior | N/A | Priority 2 | Navigational Issue | At the interior of the exit door: provide tactile exit signs with raised characters and braille at the existing main exit door and the new accessible main exit door. Provide a directional sign indicating the location of the nearest accessible emergency exit at the inaccessible exit. Provide an illuminated sign with the International Symbol of Accessibility at the accessible exit door. | 1 | 1580
18 | Broadacres Farm | B. Interior Access Route | A. Route < 36" wide | Kitchen Storage and Bathroom | 1 | N/A | Priority 1 | Program Access | Ensure that a clear width of 36" min. is maintained at the accessible route. Remove shelves. Route is allowed to narrow to 32 inches for a depth of 24 inches. | 1 | 0
19 | Broadacres Farm | B. Interior Access Route | E. Level changes > 1/4" | Horse Barn Entrance | 1 | N/A | Priority 1 | Program Access | Alter change in level to be 1/4" high max. | 1 | 144
20 | Broadacres Farm | B. Interior Access Route | E. Level changes > 1/4" | House - Main Entrance | 1 | N/A | Priority 1 | Program Access | Alter change in level to be 1/4" high max. | 1 | 432
21 | Broadacres Farm | B. Interior Access Route | H. Accessible route not provided | Stair | 1 | N/A | Priority 1 | Program Access | Consider locating all public programs on the first floor of the building. | 1 | 0
22 | Broadacres Farm | B. Interior Access Route | L. Vertical clearance < 80" above finished floor | Basement | B | N/A | Priority 1 | Program Access | The basement is unfinished with tripping hazards, no lighting, and has vertical clearance less than 80" above the floor in some areas. IHCD recommends not providing public programs in this area. | 1 | 0
23 | Broadacres Farm | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Dining Room | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
24 | Broadacres Farm | C. Doors, Doorways, & Gates | L. Hardware not operable with a closed fist | Access to Porch From the Living Room | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
25 | Broadacres Farm | U. Kitchens and Kitchenettes | A. Knee/toe clearance not provided at sink B. Sink > 34" high F. Countertop > 34" high | Kitchen | 1 | N/A | Priority 1 | Program Access | Provide a sink with knee and toe clearance positioned for a forward approach. Lower sink to be no higher than 34" positioned for a forward approach. Lower countertop to provide a work surface no higher than 34" positioned for a forward approach. | 1 | 3974
26 | Broadacres Farm | A. Overall Access | B. Turning space not provided C. Accessible plumbing fixtures or stalls not provided | Horse Barn Toilet Room | 1 | N/A | Priority 1 | Program Access | Add an accessible single-user toilet room. | 1 | 24604
27 | Broadacres Farm | A. Overall Access | B. Turning space not provided C. Accessible plumbing fixtures or stalls not provided | Kitchen Bathroom in the House | 1 | N/A | Priority 1 | Program Access | Provide an accessible single-user toilet room. | 1 | 24604
28 | Broadacres Farm | B. Sink | B. Toe and knee clearances not provided C. Rim or counter > 34" D. Non-compliant faucets | Kitchen Storage Area | 1 | N/A | Priority 1 | Program Access | Ensure there is a 27" knee clearance positioned for a forward approach. Relocate sink with the front of the rim or counter no higher than 34". Install faucets that do not require tight grasping, pinching, or twisting of the wrist. | 1 | 4080
1 | Camp Sewataro - Buildings |  |  | Building 1 - Door Between Rear Office and Sun Room | 1 | N/A | Priority 1 | Program Access | Note: From the sun room entrance, if the public is allowed to access the rest of the house, a lift or 17' ramp will need to be installed in this location. | 1 | 0
2 | Camp Sewataro - Buildings | C. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces C. Total # of designated van accessible spaces | Building 1 - Parking | Exterior | N/A | Priority 1 | Program Access | Provide one van accessible parking space. | 1 | 1850
3 | Camp Sewataro - Buildings | G. Entrance | B. Entrance not on an accessible route C. Directional sign to accessible entrance not provided | Building 1 - Route to Entrance | Exterior | N/A | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible entrance. | 1 | 346
4 | Camp Sewataro - Buildings | G. Entrance | B. Entrance not on an accessible route | Building 1 - Side Patio | 1 | N/A | Priority 1 | Program Access | Provide a 35' long ramp to this entrance with compliant landings. (Cost estimate for a pressure treated wood dogleg ramp to address a 35" change in level.) | 1 | 8566
5 | Camp Sewataro - Buildings | C. Off-Street Parking Lot or Garage | A. Total # of parking C. Total # of designated van accessible spaces | Building 2 | Exterior | N/A | Priority 1 | Program Access | Provide one van accessible space. | 1 | 1850
6 | Camp Sewataro - Buildings | B. Interior Access Route | E. Level changes > 1/4" | Building 2 -Main Entrance | 1 | N/A | Priority 1 | Program Access | Provide a compliant wood ramp to address the 12.5" change in level. (Cost estimate for a wood dogleg ramp.) | 1 | 5027
7 | Camp Sewataro - Buildings | G. Entrance | B. Entrance not on an accessible route Q. Hardware not operable with a closed fist | Building 2 -Main Entrance | Exterior | N/A | Priority 1 | Program Access | Provide a compliant sloped walkway to the entrance and a level platform at the entrance that provides door maneuvering clearance. Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. (Cost estimate for door hardware and a 15' long by 4' wide concrete route.) | 1 | 1864
8 | Camp Sewataro - Buildings | C. Off-Street Parking Lot or Garage | A. Total # of parking C. Total # of designated van accessible spaces | Building 4 - Parking | 1 | N/A | Priority 1 | Program Access | Provide one van accessible space. | 1 | 1850
9 | Camp Sewataro - Buildings | A. Exterior Access Route | N. Accessible route not provided | Building 4 - Main Entrance | 1 | N/A | Priority 1 | Program Access | Ensure an accessible route is provided. Provide a 6' long ramp with compliant platforms at the top and bottom. (Cost estimate for a straight concrete ramp with a 6" rise.) | 1 | 7080
10 | Camp Sewataro - Buildings | G. Entrance | Q. Hardware not operable with a closed fist | Building 4 - Main Entrance | 1 | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
11 | Camp Sewataro - Buildings | A. Exterior Access Route | H. Running slope > 1:20 (5%) | Building 4 - Route to Entrance | 1 | N/A | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:20 (5%). Route by entrance has an excessive slope due to tree roots. Address issues when designing ramp at entrance. | 1 | 0
12 | Camp Sewataro - Buildings | G. Entrance | O. Threshold > 1/2" high Q. Hardware not operable with a closed fist | Building 6 - Barn Entrance | Exterior | N/A | Priority 1 | Program Access | Alter threshold to be 1/2" high max. Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 534
13 | Camp Sewataro - Buildings | C. Off-Street Parking Lot or Garage | C. Total # of designated van accessible spaces A. Total # of parking | Building 6 -Route to Horse Stable Barn | Exterior | N/A | Priority 1 | Program Access | Provide one van accessible space. | 1 | 1850
1 | Camp Sewataro - Grounds | A. Exterior Access Route | C. Exterior route < 48" wide K. Surface is not stable, firm, and slip-resistant M. Route not maintained in operable working condition | Garden | Exterior | N/A | Priority 1 | Program Access | Ensure that a clear width of 48" min. is maintained at the accessible route. Provide and maintain a stone dust route. (Cost estimate for 180' long, 4' wide stone dust route.) | 1 | 5760
2 | Camp Sewataro - Grounds | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) H. Running slope > 1:20 (5%) | Sandbox 1 | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). Reduce running slope to be no steeper than 1:20 (5%). (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
3 | Camp Sewataro - Grounds | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) H. Running slope > 1:20 (5%) | Picnic Pavilion by Swimming Pond | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). Reduce running slope to be no steeper than 1:20 (5%). (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
4 | Camp Sewataro - Grounds | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) H. Running slope > 1:20 (5%) N. Accessible route not provided | Tennis Courts | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided to the tennis court from a site arrival point and to other areas of sport activity. Reduce cross slope to be no steeper than 1:50 (2.00%). Reduce running slope to be no steeper than 1:20 (5%). (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
5 | Camp Sewataro - Grounds | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) H. Running slope > 1:20 (5%) N. Accessible route not provided | Route to Golf Area | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route from a site arrival point and other areas of sport activity. Reduce cross slope to be no steeper than 1:50 (2.00%). Reduce running slope to be no steeper than 1:20 (5%). (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
6 | Camp Sewataro - Grounds | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) N. Accessible route not provided | Route to Men's and Women's Toilet Rooms by Swimming Pool | Exterior | N/A | Priority 1 | Program Access | Reduce cross slope to be no steeper than 1:50 (2.00%). Provide an accessible route with a surface that is stable, firm and slip resistant. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
7 | Camp Sewataro - Grounds | A. Exterior Access Route | H. Running slope > 1:20 (5%) | Sandbox 2 | Exterior | N/A | Priority 3 | Additional Access | Ensure an accessible route is provided between the site arrival point and sand box area. Reduce running slope to be no steeper than 1:20 (5%). (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
8 | Camp Sewataro - Grounds | A. Exterior Access Route | H. Running slope > 1:20 (5%) | Route to Swimming Pool and Toilet Rooms From Liberty Lane | Exterior | N/A | Priority 3 | Additional Access | Reduce running slope to be no steeper than 1:20 (5%). (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
9 | Camp Sewataro - Grounds | A. Exterior Access Route | H. Running slope > 1:20 (5%) K. Surface is not stable, firm, and slip-resistant N. Accessible route not provided | Route to Men's and Women's Toilet Rooms by Swimming Pool | Exterior | N/A | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:20 (5%). Provide an accessible surface that is stable, firm and slip resistant. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
10 | Camp Sewataro - Grounds | A. Exterior Access Route | H. Running slope > 1:20 (5%) N. Accessible route not provided | Picnic Pavilion East of Garden | Exterior | N/A | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:20 (5%). Ensure an accessible route is provided from a site arrival point to the pavilion. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
11 | Camp Sewataro - Grounds | A. Exterior Access Route | H. Running slope > 1:20 (5%) N. Accessible route not provided | Route to Men's and Women's Toilet Rooms by Swimming Pool | Exterior | N/A | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:20 (5%). Provide an accessible route with a surface that is stable, firm and slip resistant. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
12 | Camp Sewataro - Grounds | A. Exterior Access Route | J. Level changes > 1/4" | Street Hockey/ Basketball Court by Swimming Area and Camp Craft | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. (Cost estimate to patch a 4' x 4' asphalt area.) | 1 | 160
13 | Camp Sewataro - Grounds | A. Exterior Access Route | J. Level changes > 1/4" | Golf Area | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. (Cost estimate for 5' by 5' asphalt area.) | 1 | 250
14 | Camp Sewataro - Grounds | A. Exterior Access Route | J. Level changes > 1/4" | Golf Area | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. at one driving range min. (Cost estimate for 5' by 5' asphalt area.) | 1 | 250
15 | Camp Sewataro - Grounds | A. Exterior Access Route | K. Surface is not stable, firm, and slip-resistant | Camp Craft Pavilion | Exterior | N/A | Priority 3 | Additional Access | Provide a surface at the pavilion that is stable, firm and slip resistant. Surface is currently sand. (Cost for 20' long 4' wide stone dust route.) | 1 | 640
16 | Camp Sewataro - Grounds | A. Exterior Access Route | K. Surface is not stable, firm, and slip-resistant | Route to Swimming Pool and Toilet Rooms From Liberty Lane | Exterior | N/A | Priority 3 | Additional Access | Remove pavers and install a stone dust route with a running slope no greater than 1:20 (5%). (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
17 | Camp Sewataro - Grounds | A. Exterior Access Route | M. Route not maintained in operable working condition N. Accessible route not provided | Sandbox 1 | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route between the site arrival point and sand box area. Ensure the accessible route is maintained in operable working condition. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
18 | Camp Sewataro - Grounds | A. Exterior Access Route | N. Accessible route not provided | West Garden Entrance | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route between the garden and a site arrival point. Ensure it is stable, firm and slip-resistant. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
19 | Camp Sewataro - Grounds | A. Exterior Access Route | N. Accessible route not provided | Picnic Pavilion by Swimming Pond | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route from a site arrival point and to other program areas. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
20 | Camp Sewataro - Grounds | A. Exterior Access Route | N. Accessible route not provided | Camp Craft Pavilion | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route from a site arrival point and to other program areas. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
21 | Camp Sewataro - Grounds | A. Exterior Access Route | N. Accessible route not provided | Street Hockey/ Basketball Court by Swimming Area and Camp Craft | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route from a site arrival point and between areas of sport activity. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
22 | Camp Sewataro - Grounds | A. Exterior Access Route | N. Accessible route not provided | Kayaking, Canoeing, and Fishing Pond | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route from a site arrival point to the pond. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
23 | Camp Sewataro - Grounds | A. Exterior Access Route | N. Accessible route not provided | Gaga Ball Court | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route from a site arrival point and other amenities. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
24 | Camp Sewataro - Grounds | A. Exterior Access Route | N. Accessible route not provided | Men's and Women's Toilet Rooms by Swimming Pool Hand Sanitizer Area | Exterior | N/A | Priority 1 | Program Access | Locate hand sanitizers on an accessible route. | 1 | 0
25 | Camp Sewataro - Grounds | E. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces C. Total # of designated van accessible spaces R. Surface not stable, firm, and slip-resistant | Visitor Parking North of Camp Entrance From Haynes Road | Exterior | N/A | Priority 1 | Program Access | Provide four (4) car accessible spaces. Provide one (1) van accessible spaces. Provide a surface that is stable, firm and slip resistant such as stone dust at the accessible parking spaces. | 5 | 8260
26 | Camp Sewataro - Grounds | G. Entrance | B. Entrance not on an accessible route | Men's and Women's Toilet Rooms by Swimming Pool | Exterior | N/A | Priority 1 | Program Access | Provide a ramp to the entrance. (Cost estimate for a 15' long straight concrete ramp with compliant platforms at the top and bottom.) | 1 | 17702
27 | Camp Sewataro - Grounds | H. Emergency Exit | A. Tactile sign not provided at emergency exit C. Illuminated International Symbol of Acc. not provided (MAAB) | Toilet Rooms by Swimming Pool | 1 | N/A | Priority 2 | Navigational Issue | Provide a sign with raised characters ad braille at the emergency exit. After the exit is made accessible provide an illuminated sign with the International Symbol of Accessibility (ISA). | 1 | 1116
28 | Camp Sewataro - Grounds | B. Doors, Doorways, & Gates | N. Hardware not operable with a closed fist | Men's and Women's Toilet Rooms by Swimming Pool | Exterior | N/A | Priority 3 | Additional Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
29 | Camp Sewataro - Grounds | E. Signage | Accessible route not provided M. Text size non-compliant | Gaga Ball Court | Exterior | N/A | Priority 1 | Program Access | Provided an accessible route to the informational signage. Ensure that character size complies with the Character Height Table 703.5.5 in the ADA 2010 Standards. (Cost does not include accessible route.) | 1 | 346
30 | Camp Sewataro - Grounds | E. Signage | B. Raised characters not provided C. Raised characters < 48" or > 60 " above ground D. Braille not provided | Men's and Women's Toilet Rooms by Swimming Pool | Exterior | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille. Mount signs so that the baseline of the lowest tactile character is 48” min. above the finished floor and the baseline of the highest tactile character is 60” max. above the finished floor. | 1 | 346
31 | Camp Sewataro - Grounds | L. Benches | A. No accessible route to one bench in this area | Center of Garden | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to at least one (1)bench in this area. (Cost estimate for 6' long, 4' wide stone dust route from the walkway.) | 1 | 192
32 | Camp Sewataro - Grounds | L. Benches | A. No accessible route to one bench in this area | Street Hockey/ Basketball Court by Swimming Area and Camp Craft | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to at least one (1)bench in this area. (Cost estimate for 10' long, 4' wide stone dust walkway from the court.) | 1 | 320
33 | Camp Sewataro - Grounds | L. Benches | A. No accessible route to one bench in this area | Golf Area | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to at least one (1)bench in this area. (Cost estimate for 10' long, 4' wide stone dust walkway from the golf area.) | 1 | 320
34 | Camp Sewataro - Grounds | L. Benches | A. No accessible route to one bench in this area | Golf Area | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to at least one (1)bench in this area. (Cost estimate for 10' long, 4' wide stone dust walkway from the golf area.) | 1 | 320
35 | Camp Sewataro - Grounds | A. Overall Access | B. Turning space not provided C. Accessible plumbing fixtures or stalls not provided | Men's and Women's Toilet Rooms by Swimming Pool | 1 | N/A | Priority 1 | Program Access | Provide one accessible wheelchair compartment for women and one for men. | 2 | 12364
36 | Camp Sewataro - Grounds | A. Drinking Fountains | A. Fountain not on accessible route C. Operable parts malfunctioning E. Spout < 38" or > 43" (standing users) J. No drinking fountain provided for seated users | Near Lacrosse Field | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to drinking fountains. Repair drinking fountains. Provide a drinking fountain for standing users with the spout between 38"- 43" above the finished floor or ground. Provide a drinking fountain for seated users with a 27" high knee clearance or install a Hi-Lo drinking fountain. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 4216
37 | Camp Sewataro - Grounds | A. Drinking Fountains | A. Fountain not on accessible route C. Operable parts malfunctioning E. Spout < 38" or > 43" (standing users) J. No drinking fountain provided for seated users | Near Garden Entrance | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to drinking fountains. Repair drinking fountains. Provide a drinking fountain for standing users with the spout between 38"- 43" above the finished floor or ground. Provide a drinking fountain for seated users with a 27" high knee clearance or install a Hi-Lo drinking fountain. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 4216
38 | Camp Sewataro - Grounds | A. Drinking Fountains | A. Fountain not on accessible route C. Operable parts malfunctioning E. Spout < 38" or > 43" (standing users) J. No drinking fountain provided for seated users | Drinking Fountains by Tennis Courts | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to drinking fountains. Repair drinking fountains. Provide a drinking fountain for standing users with the spout between 38"- 43" above the finished floor or ground. Provide a drinking fountain for seated users with a 27" high knee clearance or install a Hi-Lo drinking fountain. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 4216
39 | Camp Sewataro - Grounds | A. Drinking Fountains | A. Fountain not on accessible route C. Operable parts malfunctioning E. Spout < 38" or > 43" (standing users) J. No drinking fountain provided for seated users | Near Swimming Pond | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to drinking fountains. Repair drinking fountains. Provide a drinking fountain for standing users with the spout between 38"- 43" above the finished floor or ground. Provide a drinking fountain for seated users with a 27" high knee clearance or install a Hi-Lo drinking fountain. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 4216
40 | Camp Sewataro - Grounds | C. Field | A. Accessible spaces are not provided at team seating | Softball Field | Exterior | N/A | Priority 1 | Program Access | Provide a 36" x 48" clear floor space at team seating. (Cost estimate for 3' x 4' stone dust area.) | 1 | 96
41 | Camp Sewataro - Grounds | C. Field | C. Not connected to an accessible-route | Soccer Fields | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the soccer field from a site arrival point. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
42 | Camp Sewataro - Grounds | C. Field | C. Not connected to an accessible-route | Softball Field | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the softball field from a site arrival point and other areas of sport activity. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
43 | Camp Sewataro - Grounds | C. Field | C. Not connected to an accessible-route | Fox Field Sports | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the sports field a site arrival point and other areas of sport activity. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
44 | Camp Sewataro - Grounds | C. Field | C. Not connected to an accessible-route H. Running slope > 1:20 (5%) | Lacrosse Field | Exterior | N/A | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:20 (5%). Provide an accessible route to the field from a site arrival point. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
45 | Camp Sewataro - Grounds | D. Court | C. Not connected to accessible route | Volleyball Court | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the volleyball field from a site arrival point and other areas of sport activity. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
46 | Camp Sewataro - Grounds | D. Court | C. Not connected to accessible route | Gaga Ball Court | Exterior | N/A | Priority 1 | Program Access | Provide an accessible entrance into the gaga ball court that is 32" wide min. clear and has a change in level no greater than 1/2". | 1 | 0
47 | Camp Sewataro - Grounds | D. Court | C. Not connected to accessible route K. Surface is not stable, firm, and slip-resistant | Street Hockey/ Basketball Court by Tennis Court | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the street hockey/basketball court from a site arrival point and other areas of sport activity. (Cost does not include an accessible route. Accessible routes will require further study.) | 1 | 0
48 | Camp Sewataro - Grounds | N/A | N/A | Liberty Lane To Main Area of Camp | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing signage that is visible to visitors while driving through the entrance. Existing signage is difficult to read. | 1 | 0
49 | Camp Sewataro - Grounds | N/A | N/A | Golf Area and Other Locations | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing some benches with backs and some with arms. Recommend providing clear floor space alongside benches so that a person using a wheelchair can sit shoulder to shoulder with a person seated on the bench. | 1 | 0
50 | Camp Sewataro - Grounds | N/A | N/A | West and East Garden Entrances | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a 10" high solid surface (kickplate) on the push side of each gate. | 1 | 0
1 | Davis Field | A. Exterior Access Route | H. Running slope > 1:20 (5%) N. Accessible route not provided | Entrance Near Picnic Table on West Side | Exterior | N/A | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:20 (5%). Ensure an accessible route is provided. (Cost estimate for a 6' long, 4' wide stone dust route.) | 1 | 192
2 | Davis Field | A. Exterior Access Route | H. Running slope > 1:20 (5%) N. Accessible route not provided | Center Entrance to Wayside | Exterior | N/A | Priority 1 | Program Access | Reduce running slope to be no steeper than 1:20 (5%). Ensure an accessible route is provided. (Cost estimate for a 4' wide 14' long stone dust route.) | 1 | 448
3 | Davis Field | A. Exterior Access Route | N. Accessible route not provided | Wayside and Trash Container | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided. (Cost estimate for a 4' wide 13' long stone dust route.) | 1 | 416
4 | Davis Field | E. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces | Parking Lot | Exterior | N/A | Priority 1 | Program Access | Parking lot has 175-200 spaces estimated. Provide three additional accessible spaces. | 3 | 800
5 | Davis Field | E. Off-Street Parking Lot or Garage | G. Access aisle not provided | Parking Lot Near Picnic Table on West Side | Exterior | N/A | Priority 1 | Program Access | Provide a marked access aisle that is at least 60" wide. | 1 | 300
6 | Davis Field | E. Off-Street Parking Lot or Garage | G. Access aisle not provided | Parking Lot Near Gate Opening on East Side | Exterior | N/A | Priority 1 | Program Access | Provide a marked access aisle that is at least 60" wide and a marked vehicle space that is 96" wide min. | 1 | 300
7 | Davis Field | E. Off-Street Parking Lot or Garage | G. Access aisle not provided O. Sign does not have the designation "Van Accessible" | Parking Lot Near Wayside Opening in Center | Exterior | N/A | Priority 1 | Program Access | Provide a marked access aisle that is at least 96" wide. Add the designation "Van Accessible" to the sign located at the van accessible space. | 1 | 800
8 | Davis Field | G. Operable Parts | A. Element not on an accessible route D. Side reach > 54" | Lost and Found on Back of Wayside | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the lost an found area. Relocate lost and found between 15" - 48" above the finished floor. (Cost estimate for a 20' long 4' wide stone dust route.) | 1 | 640
9 | Davis Field | J. Picnic Tables | G. Toe or knee clearance at table not provided H. Picnic table not on an accessible route | Picnic Table Near Parking Lot | Exterior | N/A | Priority 1 | Program Access | Provide at least one picnic table with top between 28"- 34" above the ground and 27" clear height underneath. Ensure that the dining surface is connected to an accessible route. (Cost estimate for an accessible picnic table and a 37" long by 4' wide stone dust path from the entrance to the table.) | 1 | 2584
10 | Davis Field | L. Benches | A. No accessible route to one bench in this area | Bench Near Parking Lot | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to at least one bench in this area. (Cost estimate for a 30' long, 4' wide stone dust route). | 1 | 960
11 | Davis Field | C. Field | C. Not connected to an accessible-route | Soccer Nets by Parking Lot and Benches | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the field. (Cost estimate for 10' long, 4' wide stone dust route.) | 1 | 320
12 | Davis Field | N/A | N/A | Picnic Table Near Parking Lot | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a 48" wide min. stable, firm and slip resistant surface under and around an accessible picnic table once it is placed in the picnic area and connected to an accessible route. | 1 | 0
13 | Davis Field | N/A | N/A | Bench Near Parking Lot | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing clear floor space of 36" wide minimum by 48" deep alongside one bench so that a wheelchair user can sit alongside someone sitting on the bench. | 1 | 0
1 | Featherland Park | A. Exterior Access Route | C. Exterior route < 48" wide | Path Between Baseball Field 1 and Softball Field 2 (Gate Closed) | Exterior | N/A | Priority 1 | Program Access | Ensure that gate is opened during operating hours. | 1 | 0
2 | Featherland Park | A. Exterior Access Route | J. Level changes > 1/4" | Asphalt Path to Entrance to Baseball Field 3 | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. | 1 | 320
3 | Featherland Park | A. Exterior Access Route | J. Level changes > 1/4" M. Route not maintained in operable working condition | Ice Rink Entrance | Exterior | N/A | Priority 1 | Program Access | Alter change in level to be 1/4" high max. Ensure the accessible route is maintained in operable working condition. | 1 | 160
4 | Featherland Park | A. Exterior Access Route | M. Route not maintained in operable working condition | Ice Rink Entrance | Exterior | N/A | Priority 1 | Program Access | Ensure the accessible route is maintained in operable working condition. | 1 | 160
5 | Featherland Park | A. Exterior Access Route | N. Accessible route not provided | South Side of South Concession Between Field 1 and Field 2 | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the toilet room, concession stand and office on the south side of the concession stand. (Cost estimate for 54' long, 4' wide asphalt route.) | 1 | 2160
6 | Featherland Park | A. Exterior Access Route | N. Accessible route not provided | Wayside Signage and Dog Waste Bin Next to Baseball Field 1 | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided. (Cost estimate for a 15' long by 4' wide asphalt route.) | 1 | 600
7 | Featherland Park | E. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces | Parking Lot by Tennis Courts and Ice Rink | Exterior | N/A | Priority 1 | Program Access | Provide three car accessible parking spaces and one van accessible parking space in this lot. As best practice, locate at least one of each accessible space by the ice rink, one by the north tennis court and one by the south tennis court. | 4 | 3200
8 | Featherland Park | E. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces O. Sign does not have the designation "Van Accessible" | North (Lower Featherland) Parking Lot | Exterior | N/A | Priority 1 | Program Access | Add the designation "Van Accessible" to one of the parking spaces. | 1 | 500
9 | Featherland Park | G. Entrance | B. Entrance not on an accessible route | South Tennis Court, North Door by Parking Lot, and North and South Doors by Concord Road | Exterior | N/A | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible entrance. | 3 | 1038
10 | Featherland Park | G. Entrance | B. Entrance not on an accessible route | North Tennis/ Basketball Court, Door on South by Concord Road | Exterior | N/A | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible entrance. | 1 | 346
11 | Featherland Park | G. Entrance | B. Entrance not on an accessible route | North Tennis/ Basketball Court, Path to the North Entrance by the Parking Lot | Exterior | N/A | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible entrance. | 1 | 346
12 | Featherland Park | G. Entrance | B. Entrance not on an accessible route | North Tennis/ Basketball Court, Path to the South Entrance by the Parking Lot | Exterior | N/A | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible entrance. | 1 | 346
13 | Featherland Park | G. Entrance | D. International Symbol of Acc. not provided | South Tennis Court, South Door by Parking Lot (Accessible) | Exterior | N/A | Priority 1 | Program Access | Provide a sign with the International Symbol of Accessibility (ISA). | 1 | 346
14 | Featherland Park | G. Entrance | D. International Symbol of Acc. not provided | North Tennis/ Basketball Court, Door on North by Concord Road | Exterior | N/A | Priority 1 | Program Access | Provide a sign with the International Symbol of Accessibility (ISA). | 1 | 346
15 | Featherland Park | G. Entrance | O. Threshold is > 1/2" high | Men's Toilet Room in South Concession Between Field 1 and Field 2 | Exterior | N/A | Priority 3 | Additional Access | Provide an asphalt walkway to the step that is sloped no greater than 1:20 (5%). Cost estimate for 10' long by 4' wide asphalt walkway. | 1 | 400
16 | Featherland Park | G. Entrance | Q. Hardware not operable with a closed fist | Women's Toilet Room in South Concession Between Field 1 and Field 2 | Exterior | N/A | Priority 3 | Additional Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
17 | Featherland Park | A. Interior Access Route | A. Route < 36" wide | South Concession Stand Women's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the lavatory when the toilet room is under renovation to add an accessible compartment. 36" clear is required when the depth is greater than 24". | 1 | 0
18 | Featherland Park | A. Interior Access Route | A. Route < 36" wide | South Concession Stand Men's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Ensure that a clear width of 36" min. is maintained at the lavatory when the toilet room is under renovation to add an accessible compartment. 36" clear is required when the depth is greater than 24". | 1 | 0
19 | Featherland Park | B. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | South Concession Stand Women's Toilet Room Exit to the Exterior | 1 | N/A | Priority 3 | Additional Access | Provide an automatic door opener. | 1 | 3060
20 | Featherland Park | B. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | South Concession Stand Men's Toilet Room Exit to the Exterior | 1 | N/A | Priority 3 | Additional Access | Provide an automatic door opener. | 1 | 3060
21 | Featherland Park | B. Doors, Doorways, & Gates | L. Threshold > 1/2" high | North (Lower Featherland) Concession Stand AED | Exterior | N/A | Priority 3 | Additional Access | Alter the threshold to be 1/2" high max. | 1 | 150
22 | Featherland Park | B. Doors, Doorways, & Gates | L. Threshold > 1/2" high | North (Lower Featherland) Concession Stand Women's Toilet Room | Exterior | N/A | Priority 3 | Additional Access | Alter the threshold to be 1/2" high max. | 1 | 150
23 | Featherland Park | B. Doors, Doorways, & Gates | L. Threshold > 1/2" high | North (Lower Featherland) Concession Stand Men's Toilet Room | Exterior | N/A | Priority 3 | Additional Access | Alter the threshold to be 1/2" high max. | 1 | 150
24 | Featherland Park | B. Doors, Doorways, & Gates | N. Hardware not operable with a closed fist | North (Lower Featherland) Concession Stand AED | Exterior | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
25 | Featherland Park | B. Doors, Doorways, & Gates | N. Hardware not operable with a closed fist | Men's Toilet Room in South Concession Between Field 1 and Field 2 | Exterior | N/A | Priority 1 | Program Access | Provide hardware that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist. | 1 | 484
26 | Featherland Park | E. Signage | B. Raised characters not provided D. Braille not provided G. Sign not located on the latch side of the door | Men's Toilet Room in South Concession Between Field 1 and Field 2 | Exterior | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille. Locate sign at permanent rooms alongside the door on the latch side. | 1 | 232
27 | Featherland Park | E. Signage | B. Raised characters not provided D. Braille not provided G. Sign not located on the latch side of the door | Women's Toilet Room in South Concession Between Field 1 and Field 2 | Exterior | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille. Locate sign at permanent rooms alongside the door on the latch side. | 1 | 232
28 | Featherland Park | E. Signage | B. Raised characters not provided D. Braille not provided G. Sign not located on the latch side of the door | North (Lower Featherland) Concession Stand Women's Toilet Room | Exterior | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille. Locate sign at permanent rooms alongside the door on the latch side. | 1 | 232
29 | Featherland Park | E. Signage | B. Raised characters not provided D. Braille not provided G. Sign not located on the latch side of the door | North (Lower Featherland) Concession Stand Men's Toilet Room | Exterior | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille. Locate sign at permanent rooms alongside the door on the latch side. | 1 | 232
30 | Featherland Park | F. Service Counter | B. Counter > 36" high | South Concession Stand | 1 | N/A | Priority 3 | Additional Access | Provide a counter that is 36" max. above the ground. | 1 | 880
31 | Featherland Park | F. Service Counter | B. Counter > 36" high | South Concession Between Field 1 and Field 2 | Exterior | N/A | Priority 3 | Additional Access | Provide a counter that is 36" max. above the ground. | 1 | 880
32 | Featherland Park | J. Picnic Tables | G. Toe or knee clearance at table not provided | Picnic Area in Front of North Concession Stand in Lower Featherland Park | Exterior | N/A | Priority 1 | Program Access | Provide at least one picnic table with top between 28"- 34" above the ground and 27" clear height underneath. | 1 | 1400
33 | Featherland Park | Q. Trash / Recycling | D. Trash container not connected to an accessible route | South Tennis Court, North Door by Parking Lot | Exterior | N/A | Priority 1 | Program Access | Ensure trash container is located on an accessible route. | 1 | 0
34 | Featherland Park | Q. Trash / Recycling | D. Trash container not connected to an accessible route | Edge of Softball Field 2 | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to trash container. (Cost estimate for a 6' long, 4' wide stone dust route.) | 1 | 192
35 | Featherland Park | A. Overall Access | C. Accessible plumbing fixtures or stalls not provided | South Concession Stand Women's Toilet Room | 1 | N/A | Priority 1 | Program Access | Provide one accessible wheelchair compartment. | 1 | 6182
36 | Featherland Park | A. Overall Access | C. Accessible plumbing fixtures or stalls not provided | South Concession Stand Men's Toilet Room | 1 | N/A | Priority 1 | Program Access | Provide one accessible wheelchair compartment. | 1 | 6182
37 | Featherland Park | B. Lavatory | B. Toe or knee clearances not provided D. Faucet not operable with a closed fist | South Concession Stand Women's Toilet Room | 1 | N/A | Priority 1 | Program Access | Provide knee and toe clearance positioned for a forward approach. Provide a faucet that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist at lavatory. | 1 | 2672
37 | Featherland Park | B. Lavatory | E. Exposed plumbing underneath | South Concession Stand Women's Toilet Room | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at lavatory. | 1 | 92
38 | Featherland Park | B. Lavatory | B. Toe or knee clearances not provided D. Faucet not operable with a closed fist | South Concession Stand Men's Toilet Room | 1 | N/A | Priority 1 | Program Access | Provide knee and toe clearance positioned for a forward approach. Provide a faucet that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist at lavatory. | 1 | 2672
38 | Featherland Park | B. Lavatory | E. Exposed plumbing underneath | South Concession Stand Men's Toilet Room | 1 | N/A | Priority 1 | Safety | Insulate or otherwise configure pipes to prevent contact at lavatory. | 1 | 92
39 | Featherland Park | E. Urinal | A. Rim > 17" high | South Concession Stand Men's Toilet Room | 1 | N/A | Priority 1 | Program Access | Provide at least one urinal with the rim no higher than 17" above the finished floor. | 1 | 3248
40 | Featherland Park | F. Dispensers | A. Controls > 42" (MAAB) E. Dispenser acts as a protruding object | South Concession Stand Women's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Relocate the paper towel dispenser so that the operable part is 42" max. above the finished floor and out of the circulation path. | 1 | 256
41 | Featherland Park | C. Field | A. Accessible spaces are not provided at team seating | Baseball Field 1 Entrance Team Seating Area 1 | Exterior | N/A | Priority 1 | Program Access | Relocate bench to provide a 36" x 48" clear floor space at team seating. Provide a stone dust surface at accessible team seating space. | 1 | 96
42 | Featherland Park | C. Field | A. Accessible spaces are not provided at team seating | Baseball Field 1 Entrance Team Seating Area 2 | Exterior | N/A | Priority 1 | Program Access | Relocate bench to provide a 36" x 48" clear floor space at team seating. Provide a stone dust surface at accessible team seating space. | 1 | 96
43 | Featherland Park | C. Field | A. Accessible spaces are not provided at team seating | Baseball Field 5 Team Seating 1 | Exterior | N/A | Priority 1 | Program Access | Relocate bench to provide a 36" x 48" clear floor space at team seating. Provide a stone dust surface at accessible team seating space. | 1 | 96
44 | Featherland Park | C. Field | A. Accessible spaces are not provided at team seating | Baseball Field 5 Team Seating 2 | Exterior | N/A | Priority 1 | Program Access | Provide a a 36" x 48" stone dust surface at accessible team seating space. | 1 | 96
45 | Featherland Park | C. Field | A. Accessible spaces are not provided at team seating | Baseball Field 4 Team Seating 1 | Exterior | N/A | Priority 1 | Program Access | Relocate bench to provide a 36" x 48" clear floor space at team seating. Provide a stone dust surface at accessible team seating space. | 1 | 96
46 | Featherland Park | C. Field | A. Accessible spaces are not provided at team seating | Baseball Field 4 Team Seating 2 | Exterior | N/A | Priority 1 | Program Access | Relocate bench to provide a 36" x 48" clear floor space at team seating. Provide a stone dust surface at accessible team seating space. | 1 | 96
47 | Featherland Park | C. Field | A. Accessible spaces are not provided at team seating | Baseball Field 3, Team Seating 1 | Exterior | N/A | Priority 1 | Program Access | Provide a a 36" x 48" stone dust surface at accessible team seating space alongside the bench. | 1 | 96
48 | Featherland Park | C. Field | A. Accessible spaces are not provided at team seating | Baseball Field 3, Team Seating 2 | Exterior | N/A | Priority 1 | Program Access | Relocate bench to provide a 36" x 48" clear floor space at team seating. Provide a stone dust surface at accessible team seating space. | 1 | 96
49 | Featherland Park | C. Field | B. Accessible spaces not provided at sidelines seating | Baseball Field 4 Bleacher | Exterior | N/A | Priority 1 | Program Access | Provide a 36" x 48" clear floor space on each side of the bleacher. (Cost estimate for 15' long, 4' wide stone dust route.) | 2 | 960
50 | Featherland Park | C. Field | B. Accessible spaces not provided at sidelines seating | Baseball Field 3 Bleacher | Exterior | N/A | Priority 1 | Program Access | Provide a 36" x 48" clear floor space on each side of the bleacher. (Cost estimate for 15' long, 4' wide stone dust route.) | 2 | 960
51 | Featherland Park | C. Field | B. Accessible spaces not provided at sidelines seating C. Not connected to an accessible-route | Baseball Field 1 Bleachers Near Team Seating Area 1 | Exterior | N/A | Priority 1 | Program Access | Provide a 36" x 48" clear floor space on each side of the bleacher. Provide an accessible route to the bleacher. (Cost estimate for 95' long, 4' wide stone dust route.) | 1 | 3040
52 | Featherland Park | C. Field | B. Accessible spaces not provided at sidelines seating C. Not connected to an accessible-route | Baseball Field 1 Bleachers near Team Seating 2 | Exterior | N/A | Priority 1 | Program Access | Provide a 36" x 48" clear floor space on each side of the bleacher. Provide an accessible route to the bleacher. (Cost estimate for 103' long, 4' wide stone dust route.) | 1 | 3296
53 | Featherland Park | C. Field | B. Accessible spaces not provided at sidelines seating C. Not connected to an accessible-route | Adult Softball Field 2 Bleachers on South | Exterior | N/A | Priority 1 | Program Access | Provide a 36" x 48" clear floor space on each side of each bleacher. Provide an accessible route to the accessible seating area. (Cost estimate for 18' long, 4' wide stone dust route.) | 4 | 2304
54 | Featherland Park | C. Field | B. Accessible spaces not provided at sidelines seating C. Not connected to an accessible-route | Baseball Field 5 Bleacher | Exterior | N/A | Priority 1 | Program Access | Relocate bleacher to an accessible route closer to the asphalt. Provide a level 36" x 48" clear floor space on each side of the bleacher. Provide an accessible route to the field. (Cost estimate for 4' long, 4' wide stone dust route.) | 2 | 256
55 | Featherland Park | C. Field | C. Not connected to an accessible-route | Baseball Field 1 Entrance | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the field and to each team seating area. (Cost estimate for 200' long, 4' wide stone dust walkway.) | 1 | 6400
56 | Featherland Park | C. Field | C. Not connected to an accessible-route | Path to Baseball Field 5 Team Seating | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the baseball field, including to the team seating areas. (Cost estimate for 210' long, 4' wide stone dust route.) | 1 | 6720
57 | Featherland Park | C. Field | C. Not connected to an accessible-route | Entrance to Baseball Field 4 | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the field and team seating areas. (Cost estimate for 120' long, 4' wide stone dust route.) | 1 | 3840
58 | Featherland Park | C. Field | C. Not connected to an accessible-route J. Level changes > 1/4" | Adult Softball Field 2 Team Seating Areas | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to each team seating area. Ensure that level changes are no greater than 1/4" high. (Cost estimate for 12' long, 4' wide asphalt route.) | 2 | 960
59 | Featherland Park | C. Field | D. Practice areas are not on an accessible route | Adult Softball Field 2 Pitching Area on South Side | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the pitching area on the south side. (Cost estimate for 20' long by 4' wide stone dust route.) | 1 | 640
60 | Featherland Park | C. Field | D. Practice areas are not on an accessible route | Adult Softball Field 2 Pitching Practice on West Side | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the pitching area on the west side. (Cost estimate for 10' long, 4' wide stone dust route.) | 1 | 320
61 | Featherland Park | C. Field | D. Practice areas are not on an accessible route | Batting Cage | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to practice areas. (Cost estimate for 54' long, 4' wide stone dust route.) | 1 | 1728
62 | Featherland Park | C. Field | F. No accessible route to all areas of sport activity | Entrance to Baseball Field 3 | Exterior | N/A | Priority 1 | Program Access | Install an accessible route between all areas of sports activity including the team the field, team seating area and batting cage. (Cost estimate for 200' long, 4' wide stone dust route.) | 1 | 6400
63 | Featherland Park | N/A | N/A | Bench Near Baseball Field 5 | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing clear floor space of 36" wide minimum by 48" deep alongside one bench so that a wheelchair user can sit alongside someone sitting on the bench. | 1 | 0
1 | Feeley Field | A. Exterior Access Route | M. Route not maintained in operable working condition J. Level changes > 1/4" | Sidewalk Between South Softball and Baseball Fields to North Concession Stand | Exterior | N/A | Priority 1 | Program Access | Alter change in level to be 1/4" high max. Ensure the accessible route is maintained in operable working condition. | 1 | 160
2 | Feeley Field | A. Exterior Access Route | N. Accessible route not provided | North Concession Stand and Toilet Room Building | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided. (Cost estimate for 50' long concrete ramp to the building.) | 1 | 59007
3 | Feeley Field | A. Exterior Access Route | N. Accessible route not provided | Signage at Tennis Court | Exterior | N/A | Priority 1 | Program Access | Relocate wayside sign to an accessible route. | 1 | 0
4 | Feeley Field | A. Exterior Access Route | N. Accessible route not provided | Southwest Tennis Entrance From North Softball Field | Exterior | N/A | Priority 1 | Program Access | Install an accessible route between all areas of sport activity. (Cost estimate for 6' long by 4' wide stone dust route.) | 1 | 192
5 | Feeley Field | E. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces C. Total # of designated van accessible spaces | Parking Lot by Tennis Courts | Exterior | N/A | Priority 1 | Program Access | Provide one van accessible parking space and one car accessible parking space by the northwest entrance. (Cost of one accessible space, access aisle, sign and striping, including leveling space.) | 2 | 3700
6 | Feeley Field | E. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces C. Total # of designated van accessible spaces | Unpaved Lot by North Softball Field | Exterior | N/A | Priority 1 | Program Access | Provide four car accessible parking spaces and one van accessible parking space. (Cost estimate for signage and striping.) | 5 | 4000
7 | Feeley Field | E. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces G. Access aisle not provided O. Sign does not have the designation "Van Accessible" | Parking Lot by Southwest Softball Field, Accessible Parking Area | Exterior | N/A | Priority 1 | Program Access | Provide a marked access aisle for one car accessible and one van accessible parking space. Add the designation "Van Accessible" to the sign located at the van accessible space. | 1 | 1100
8 | Feeley Field | G. Entrance | B. Entrance not on an accessible route | Northwest Tennis Entry | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route into the tennis court from the parking lot. (Cost estimate based on a 30' long concrete ramp with handrails). | 1 | 35404
9 | Feeley Field | G. Entrance | C. Directional sign to accessible entrance not provided | North Center Tennis Entrance | Exterior | N/A | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible entrance. | 1 | 346
10 | Feeley Field | G. Entrance | C. Directional sign to accessible entrance not provided | Northeast Tennis Entry | Exterior | N/A | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible entrance. | 1 | 346
11 | Feeley Field | G. Entrance | D. International Symbol of Acc. not provided | Northwest Tennis Entrance | Exterior | N/A | Priority 1 | Program Access | After entrance is made accessible provide signage with the International Symbol of Accessibility (ISA). | 1 | 346
12 | Feeley Field | G. Entrance | D. International Symbol of Acc. not provided | Tennis Entrances on South | Exterior | N/A | Priority 1 | Program Access | After an accessible route is made to both south entrances, provide a sign with the International Symbol of Accessibility (ISA) at each gate. | 2 | 692
13 | Feeley Field | B. Doors, Doorways, & Gates | C. Maneuvering clearance(s) not provided | Women's Toilet Room | 1 | N/A | Priority 3 | Additional Access | Provide an automatic door opener. | 1 | 3060
14 | Feeley Field | B. Doors, Doorways, & Gates | L. Threshold > 1/2" high | Women's and Men's Toilet Room Doors | Exterior | N/A | Priority 3 | Additional Access | Threshold is 6" to 10" at the men's and women's toilet room. Recommend providing a raised walkway around building to connect concession counters, and toilet rooms. (Cost estimate based on 107' long, 4' wide min. walkway around building so that the maximum door threshold to both toilet rooms is 1/2 inch. | 1 | 6848
15 | Feeley Field | E. Signage | B. Raised characters not provided D. Braille not provided G. Sign not located on the latch side of the door | Men's Toilet Room | Exterior | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille. Locate sign at permanent rooms alongside the door on the latch side. | 1 | 232
16 | Feeley Field | E. Signage | B. Raised characters not provided D. Braille not provided G. Sign not located on the latch side of the door | Women's Toilet Room | Exterior | N/A | Priority 2 | Navigational Issue | Provide text with raised characters duplicated in braille. Locate sign at permanent rooms alongside the door on the latch side. | 1 | 232
17 | Feeley Field | F. Service Counter | A. Not connected to a accessible route B. Counter > 36" high | North Concession Stand | Exterior | N/A | Priority 1 | Program Access | Ensure the counter is connected to an accessible route. Provide a counter that is 36" max. above the ground. (Note: If a raised walkway or plinth is built around the building, concession counter may not need to be lowered.) | 1 | 880
18 | Feeley Field | F. Service Counter | A. Not connected to a accessible route B. Counter > 36" high | North Concession Stand | Exterior | N/A | Priority 1 | Program Access | Ensure the counter is connected to an accessible route. Provide a counter that is 36" max. above the ground. (Note: If a raised walkway or plinth is built around the building, concession counter may not need to be lowered.) | 1 | 880
19 | Feeley Field | F. Service Counter | B. Counter > 36" high | Baseball Field Concession Stand | Exterior | N/A | Priority 3 | Additional Access | Provide a counter that is 36" max. above the ground. | 1 | 880
20 | Feeley Field | J. Picnic Tables | G. Toe or knee clearance at table not provided | North Concession Stand Picnic Area | Exterior | N/A | Priority 1 | Program Access | Provide at least one picnic table with top between 28"- 34" above the ground and 27" clear height underneath. Ensure it is located on an accessible route. | 1 | 1400
21 | Feeley Field | L. Benches | A. No accessible route to one bench in this area | Seating at North Softball Field | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to at least one bench in this area. (Cost estimate for 4' long by 4' wide stone dust route.) | 1 | 128
22 | Feeley Field | Q. Trash / Recycling | D. Trash container not connected to an accessible route | North Center Tennis Entrance | Exterior | N/A | Priority 1 | Program Access | Ensure trash container is located on an accessible route. | 1 | 0
23 | Feeley Field | A. Overall Access | C. Accessible plumbing fixtures or stalls not provided B. Toe or knee clearances not provided D. Faucet not operable with a closed fist E. Exposed plumbing underneath lavatory A. Urinal rim > 17" high B. Clear floor space not provided at urinal C. Flush control too high or not properly located at urinal | Men's Toilet Room | 1 | N/A | Priority 1 | Program Access | Renovate toilet room to be an accessible single-user toilet room. Provide a faucet that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist for at least one lavatory. Insulate or otherwise configure pipes to prevent contact at lavatory. Provide at least one lavatory with knee and toe clearance positioned for a forward approach. | 1 | 24604
24 | Feeley Field | A. Overall Access | C. Accessible plumbing fixtures or stalls not provided D. Faucet not operable with a closed fist E. Exposed plumbing underneath | Women's Toilet Room | 1 | N/A | Priority 1 | Program Access | Renovate toilet room to be an accessible single-user toilet room. Provide a faucet that can be operable with one hand and not require tight grasping, pinching, or twisting of the wrist for at least one lavatory. Insulate or otherwise configure pipes to prevent contact at lavatory. | 1 | 24604
25 | Feeley Field | C. Field | A. Accessible spaces are not provided at team seating | North Softball Field, Team Seating Area | Exterior | N/A | Priority 1 | Program Access | Provide a 36" x 48" clear floor space at team seating alongside bench. (Cost estimate for 3' by 4' stone dust area.) | 2 | 192
26 | Feeley Field | C. Field | A. Accessible spaces are not provided at team seating C. Not connected to an accessible-route | Southeast Softball Field Team Seating | Exterior | N/A | Priority 1 | Program Access | Provide a 36" x 48" clear floor space at team seating. Provide an accessible route to the field. (Cost estimate for 420' 4' wide stone dust route from southwest softball field.) | 1 | 13440
27 | Feeley Field | C. Field | A. Accessible spaces are not provided at team seating F. No accessible route to all areas of sport activity | Southwest Softball Field Team Seating | Exterior | N/A | Priority 1 | Program Access | Provide a 36" x 48" clear floor space at each team seating area Install an accessible route to each team seating area. (Cost estimate for 216' long, 4' wide stone dust route from the parking lot.) | 1 | 6912
28 | Feeley Field | C. Field | B. Accessible spaces not provided at sidelines seating | Baseball Field, Access to Bleachers | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to team seating area from the parking lot to the north. Provide a 36" x 48" clear floor space on each side of the bleacher. (Cost estimate for 173' long, 4' wide stone dust route.) | 1 | 5536
29 | Feeley Field | C. Field | B. Accessible spaces not provided at sidelines seating | Baseball Field, Bleacher In Front of Press Box | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to sideline seating and a 36" x 48" clear floor space alongside each side of bleacher. (Cost estimate for 34' long, 4' wide stone dust route.) | 1 | 1088
30 | Feeley Field | C. Field | B. Accessible spaces not provided at sidelines seating D. Practice areas are not on an accessible route | North Softball Field Batting Cage and Spectator Seating | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to sidelines seating and provide a 36" x 48" clear floor space alongside each side of bleacher. Provide an accessible route to the batting cage. (Cost estimate for 102' long, 4' wide stone dust route.) | 1 | 3264
31 | Feeley Field | C. Field | C. Not connected to an accessible-route | Baseball Field, Entrance to North Team Seating Area | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the the north team seating area. (Cost estimate for 6' long, 4' wide asphalt route.) | 1 | 240
32 | Feeley Field | C. Field | C. Not connected to an accessible-route | Baseball Field, West Team Seating Area | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the the west team seating area. (Cost estimate for 15' long, 4' wide asphalt route.) | 1 | 600
33 | Feeley Field | C. Field | C. Not connected to an accessible-route F. No accessible route to all areas of sport activity | North Softball Field Team Seating Areas | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the field and to team seating areas. (Cost estimate for 305' long, 4' wide stone dust route.) | 1 | 9760
34 | Feeley Field | C. Field | D. Practice areas are not on an accessible route | Baseball Field, Batting Cages | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to practice areas. (Cost estimate for 12' long, 4' wide asphalt route.) | 1 | 480
35 | Feeley Field | C. Field | D. Practice areas are not on an accessible route | Baseball Field, Route Between North Team Seating Area and Pitching Practice Area | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to pitching practice area. (Cost estimate for 10' long, 4' wide asphalt route.) | 1 | 400
36 | Feeley Field | C. Field | D. Practice areas are not on an accessible route | Baseball Field, Route Between West Team Seating Area and Pitching Practice Area | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to practice areas. (Cost estimate for 12' long, 4' wide asphalt route.) | 1 | 480
37 | Feeley Field | D. Court | F. No accessible route between all areas of sport activity | Tennis Entry on Southeast From North Softball Field | Exterior | N/A | Priority 1 | Program Access | Install an accessible route between the tennis court and softball field. (Cost estimate for 4' long by 4' wide stone dust route.) | 1 | 128
38 | Feeley Field | N/A | N/A | Baseball Field, Path to Upper Level Bleachers | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing handrails at the stepped route to spectator seating. | 1 | 0
39 | Feeley Field | N/A | N/A | North Concession Stand and Toilet Rooms | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing an accessible route from this facility to the sidewalk. | 1 | 0
40 | Feeley Field | N/A | N/A | Seating at North Softball Field | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing clear floor space of 36" wide minimum by 48" deep alongside one bench so that a wheelchair user can sit alongside someone sitting on the bench. | 1 | 0
1 | Grinnell Park | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Walkway Southwest of World War I Memorial | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). (Cost based on 4'x15' of stone dust to correct slope.) | 1 | 480
2 | Grinnell Park | A. Exterior Access Route | G. Cross slope > 1:50 (2.00%) | Walkway West of World War I Memorial | Exterior | N/A | Priority 3 | Additional Access | Reduce cross slope to be no steeper than 1:50 (2.00%). (Cost based on 4'x6' of stone dust to correct slope.) | 1 | 192
3 | Grinnell Park | A. Exterior Access Route | M. Route not maintained in operable working condition | Walkway Southeast of World War I Memorial | Exterior | N/A | Priority 1 | Program Access | Ensure the accessible route is maintained in operable working condition. | 1 | 0
4 | Grinnell Park | A. Exterior Access Route | P. Detectable warning not provided | Crosswalk at the Intersection of Hudson and Concord Roads | Exterior | N/A | Priority 1 | Program Access | Provide a detectable warning on the curb ramp. | 1 | 360
5 | Grinnell Park | L. Benches | A. No accessible route to one bench in this area | Southeast End of the Park | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to at least one bench in this area. (Cost based on a new 4' wide min. x 15' stone dust path.) | 1 | 600
6 | Grinnell Park | Bench | N/A | Walkway From World War I Memorial to the Intersection of Hudson and Concord Roads | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a bench with a 36” min. x 48" min. wide stable, firm and slip resistant surface such as stone dust at one end by the pathway the runs along Hudson Road to provide a location near the memorial for visitors to rest while at the park. | 1 | 0
7 | Grinnell Park | Clear Floor Space by Bench | N/A | Southeast End of the Park | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a 36” min. x 48" min. wide stable, firm and slip resistant surface such as stone dust at one end of one of the benches in this area once the bench is connected to an accessible route. | 1 | 0
1 | Haskell Field | A. Exterior Access Route | E. Route obstructed by protruding objects | Library - Children’s Playground | Exterior | N/A | Priority 3 | Additional Access | Provide a cane-detectable barrier below book exchange 27" max. above the ground. (Book exchange protrudes 15.75".) | 1 | 306
2 | Haskell Field | A. Exterior Access Route | H. Running slope > 1:20 (5%) | Left Side Entrance From Parking 3 to Soccer Fields | Exterior | N/A | Priority 3 | Additional Access | Reduce running slope to be no steeper than 1:20 (5%), reduce change in level from parking to soccer field entrance to 1/2" max. | 1 | 0
3 | Haskell Field | A. Exterior Access Route | M. Route not maintained in operable working condition | Path to Children’s Playground | Exterior | N/A | Priority 1 | Program Access | Ensure the accessible route is maintained in operable working condition. | 1 | 0
4 | Haskell Field | A. Exterior Access Route | N. Accessible route not provided | Wayside Next to Parking 3 | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided to the wayside and the dog waste bag dispenser. Either relocate both to an accessible location or provide a firm, stable and slip resistant route to both. (Cost based on a 4' wide min. x 15' long stone dust path to both amenities.) | 1 | 480
5 | Haskell Field | A. Exterior Access Route | N. Accessible route not provided | From Right Side of Parking 1 to Accessible Path 2 | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided between the parking lot and the existing accessible path. (Cost based on a 4' wide min. x 15' firm, stable and slip resistant accessible path to the existing path.) | 1 | 960
6 | Haskell Field | E. Signage | Sign not maintained in operable working condition | Men's Toilet Room | Exterior | N/A | Priority 2 | Navigational Issue | Provide new sign with raised characters and braille. | 1 | 232
7 | Haskell Field | F. Service Counter | B. Counter > 36" high | Concession Stand - Children’s Playground | Exterior | N/A | Priority 3 | Additional Access | Provide a counter that is 36" max. above the ground. | 1 | 880
8 | Haskell Field | G. Operable Parts | C. Reach < 15" or > 48"(forward/side approach) | Wayside | Exterior | N/A | Priority 3 | Additional Access | Reposition dog waste bag dispenser to between 15"- 48" above the finished floor. | 1 | 0
9 | Haskell Field | J. Picnic Tables | G. Toe or knee clearance at table not provided | Picnic Table Near Accessible Play Structure 1 - Children’s Playground | Exterior | N/A | Priority 1 | Program Access | Provide at least one picnic table in this area with top between 28"- 34" above the ground and 27" clear height underneath. | 1 | 1400
10 | Haskell Field | J. Picnic Tables | G. Toe or knee clearance at table not provided H. Picnic table not on an accessible route | Picnic Tables Next to Parking 3 | Exterior | N/A | Priority 1 | Program Access | Provide at least one picnic table with top between 28"- 34" above the ground and 27" clear height underneath. Ensure that the dining surface is connected to an accessible route. | 1 | 1400
11 | Haskell Field | J. Picnic Tables | G. Toe or knee clearance at table not provided H. Picnic table not on an accessible route | Opening 1 Near Accessible Path 2 From Right Side of Parking 1 | Exterior | N/A | Priority 1 | Program Access | Provide at least one picnic table with top between 28"- 34" above the ground and 27" clear height underneath. Ensure that the dining surface is connected to an accessible route. (Cost based on an accessible picnic table and a 4' wide min. x 15' firm, stable and slip resistant accessible path to the picnic table.) | 1 | 2360
12 | Haskell Field | J. Picnic Tables | G. Toe or knee clearance at table not provided H. Picnic table not on an accessible route | Picnic Tables Near Parking 3 | Exterior | N/A | Priority 1 | Program Access | Provide at least one picnic table with top between 28"- 34" above the ground and 27" clear height underneath. Ensure that the accessible picnic table in this area is connected to an accessible route. | 1 | 1400
13 | Haskell Field | J. Picnic Tables | H. Picnic table not on an accessible route | Outdoor Play Gym | Exterior | N/A | Priority 1 | Program Access | Ensure that the picnic table is connected to an accessible route. (Cost based on a stone dust patch, 3'x4' min., at the accessible end of the accessible picnic table.) | 1 | 240
14 | Haskell Field | L. Benches | A. No accessible route to one bench in this area | Bench Next to Children’s Playground | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to at least one bench in this area. (Cost based on a 4' wide min. x 15' long stone dust path to bench.) | 1 | 480
15 | Haskell Field | L. Benches | A. No accessible route to one bench in this area | Baseball Seating | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to at least one bench in this area and to the trash receptacle or relocate both to an accessible route. (Cost based on a 4' wide min. x 6' firm, stable and slip resistant path to bench and trash receptacle.) | 1 | 240
16 | Haskell Field | L. Benches | A. No accessible route to one bench in this area | Right Side Soccer Field | Exterior | N/A | Priority 1 | Program Access | Install an accessible route with a 5.00% max. running and 2.00% max. cross slope between towards benches and the resumed accessible path. (Cost based on a 4' wide min. x 60' long path leading towards benches and the resumed accessible path.) | 1 | 1920
17 | Haskell Field | L. Benches | A. No accessible route to one bench in this area | Accessible Path 2 | Exterior | N/A | Priority 1 | Program Access | Install an accessible route with a 5.00% max. running and 2.00% max. cross slope between towards benches and the resumed accessible path. (Cost based on a 4' wide min. x 60' long path leading towards benches and the resumed accessible path.) | 1 | 1920
18 | Haskell Field | Q. Trash / Recycling | D. Trash container not connected to an accessible route | Left Side Entrance From Parking 3 to Soccer Fields | Exterior | N/A | Priority 1 | Program Access | Ensure trash container is located on an accessible route. | 1 | 0
19 | Haskell Field | Q. Trash / Recycling | D. Trash container not connected to an accessible route | Path 2 | Exterior | N/A | Priority 1 | Program Access | Ensure trash container is located on an accessible route. | 1 | 0
20 | Haskell Field | A. Overall Access | H. Audible and visible alarms not provided | Men's Toilet Room | Exterior | N/A | Priority 3 | Additional Access | When fire system is updated, ensure that a visible and audible fire alarm is installed. | 1 | 0
21 | Column1: Haskell Field; Column2: C. Single-User Toilet; Column4: Women's Accessible Toilet Room; Column5: Exterior; Column6: N/A; Column9: This toilet room was locked on the day that IHCD was at Haskell Field and could not be surveyed.; Column10: 1; Column11: 0
22 | Haskell Field | A. Drinking Fountains | H. No drinking fountain provided for standing users | Fountain - Children’s Playground | Exterior | N/A | Priority 1 | Program Access | Provide an additional drinking fountain for standing users or install a Hi-Lo drinking fountain. | 1 | 4028
23 | Haskell Field | B. Play Areas | B. Accessible route not provided at play components | Accessible Play Structure 2 - Children’s Playground | Exterior | N/A | Priority 1 | Program Access | Reduce change in level to 1/2" max. | 1 | 0
24 | Haskell Field | B. Play Areas | B. Accessible route not provided at play components | Play Structure 3 - Children’s Playground | Exterior | N/A | Priority 1 | Program Access | Provide a compliant impact-attenuating surface under and around the play components. Note: IHCD team has been told that Sudbury has budgeted $163,000 to address this issue at Haskell Field. | 1 | 0
25 | Haskell Field | B. Play Areas | N. Play areas not maintained in operable working condition | Near Climber | Exterior | N/A | Priority 1 | Program Access | Ensure play area is maintained in operable working condition/repair patch as needed. | 1 | 0
26 | Haskell Field | B. Play Areas | N. Play areas not maintained in operable working condition | Accessible Play Structure 2 - Children’s Playground | Exterior | N/A | Priority 1 | Program Access | Ensure play area is maintained in operable working condition. | 1 | 0
27 | Haskell Field | B. Play Areas | N. Play areas not maintained in operable working condition | Ground Play Components | Exterior | N/A | Priority 1 | Program Access | Ensure play area is maintained in operable working condition. | 1 | 0
28 | Haskell Field | C. Field | A. Accessible spaces are not provided at team seating | Path 1 Baseball Seating | Exterior | N/A | Priority 1 | Program Access | Provide a 48" wide min. firm, stable and slip resistant path to team seating with a 5.00% max. running and 2.00% max. cross slope. (Cost based on a 48" wide x 15' long stone dust path.) | 1 | 480
29 | Haskell Field | C. Field | A. Accessible spaces are not provided at team seating | Baseball Seating | Exterior | N/A | Priority 1 | Program Access | Provide a 36" x 48" clear floor space at team seating. | 1 | 0
30 | Haskell Field | C. Field | A. Accessible spaces are not provided at team seating | Baseball Seating 2 | Exterior | N/A | Priority 1 | Program Access | Provide a 36" x 48" clear floor space at team seating. | 1 | 0
31 | Haskell Field | C. Field | B. Accessible spaces not provided at sidelines seating | Bleachers | Exterior | N/A | Priority 1 | Program Access | Provide a 4' wide min. firm, stable and slip resistant route to the sideline seating bleachers with a 5.00% max. running and 2.00% max. cross slope. Provide a 36" x 48" clear floor space at sidelines seating. (Cost based on a 4' wide min. x 30' path.) | 1 | 960
32 | Haskell Field | C. Field | C. Not connected to an accessible-route | Baseball Dugout to Field | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the field. Widen gate to 32" min. | 1 | 0
33 | Haskell Field | C. Field | C. Not connected to an accessible-route | Towards Baseball Seating 2 | Exterior | N/A | Priority 1 | Program Access | Provide a 4' wide min. firm, stable and slip resistant route to the equipment storage shed, the boundary of sport activity, and to the second team seating dugout with a 5.00% max. running and 2.00% max. cross slope at baseball. (Cost based on a 4' wide min. x 60' path.) | 1 | 1920
34 | Haskell Field | C. Field | C. Not connected to an accessible-route | Baseball Seating 2 | Exterior | N/A | Priority 1 | Program Access | Reduce change in level to 1/2" max. (Cost based on a concrete patch.) | 1 | 256
35 | Haskell Field | C. Field | C. Not connected to an accessible-route | Batting Cage | Exterior | N/A | Priority 1 | Program Access | Provide a firm, stable and slip resistant accessible route to the batting cage entry with a 5.00% max. running and 2.00% max. cross slope. | 1 | 960
36 | Haskell Field | C. Field | F. No accessible route to all areas of sport activity | Right Side of Soccer Field | Exterior | N/A | Priority 1 | Program Access | Install an accessible route with a 5.00% max. running and 2.00% max. cross slope between the existing path and boundary of sport activity at the soccer field. (Cost based on a 4' wide min. x 60' long path leading towards the benches and the resumed accessible path.) | 1 | 1920
37 | Haskell Field | Bench | N/A | Bench 1 on Path 1 | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a 3'x4' asphalt patch at one end of bench. | 1 | 0
38 | Haskell Field | Bench | N/A | Bench 2 on Path 1 | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a 3'x4' asphalt patch at one end of bench. | 1 | 0
39 | Haskell Field | Bench | N/A | Path 2 | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend relocate bench closer to existing accessible route and providing a 3'x4' asphalt patch at one end of bench. | 1 | 0
40 | Haskell Field | Bench | N/A | Bench 3 on Path 2 | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a 3'x4' asphalt patch at one end of bench. | 1 | 0
41 | Haskell Field | Men's Toilet Room | N/A | Men's Toilet Room | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a sign with the International Symbol of Accessibility (ISA) at the men's toilet room. | 1 | 0
42 | Haskell Field | Picnic Table | N/A | Picnic Tables Near Parking 3 | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend proving a 48" min. firm, stable and slip resistant surface around the exterior of each accessible picnic table in the park. | 1 | 0
1 | Heritage Park | A. Exterior Access Route | C. Exterior route < 48" wide | Walkway South of Pond | Exterior | N/A | Priority 3 | Additional Access | Ensure that a clear width of 48" min. is maintained at the accessible route. (Cost estimate for labor and 20' long 4' wide stone dust route.) | 1 | 640
2 | Heritage Park | A. Exterior Access Route | C. Exterior route < 48" wide G. Cross slope > 1:50 (2.00%) H. Running slope > 1:20 (5%) | Dogwood Path | Exterior | N/A | Priority 3 | Additional Access | Ensure that a clear width of 48" min. is maintained at the accessible route. Reduce cross slope to be no steeper than 1:50 (2.00%). Reduce running slope to be no steeper than 1:20 (5%). (Cost estimate for a 530' long, 4' wide stone dust path.) | 1 | 16960
3 | Heritage Park | A. Exterior Access Route | F. Surface openings > 1/2" H. Running slope > 1:20 (5%) | 9/11 Memorial | Exterior | N/A | Priority 3 | Additional Access | Ensure that surface has openings that are 1/2" max. and the long opening dimension is perpendicular to the dominant direction of travel. Reduce running slope to be no steeper than 1:20 (5%). (Cost estimate for a 14' long 4' wide stone dust route.) | 1 | 560
4 | Heritage Park | A. Exterior Access Route | H. Running slope > 1:20 (5%) | Walkway South of Pond | Exterior | N/A | Priority 3 | Additional Access | Reduce running slope to be no steeper than 1:20 (5%). (Cost estimate for a 6' long 4' wide stone dust area.) | 1 | 240
5 | Heritage Park | A. Exterior Access Route | H. Running slope > 1:20 (5%) | Walkway South of Pond | Exterior | N/A | Priority 3 | Additional Access | Reduce running slope to be no steeper than 1:20 (5%). (Cost estimate for a 12' long 4' wide stone dust area.) | 1 | 480
6 | Heritage Park | A. Exterior Access Route | J. Level changes > 1/4" | Dogwood Path | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. (Cost estimate for providing a 12' by 4' stone dust area.) | 1 | 480
7 | Heritage Park | A. Exterior Access Route | J. Level changes > 1/4" | Dogwood Path Bridge | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. (Cost estimate for providing a 4' by 4' stone dust area.) | 1 | 160
8 | Heritage Park | A. Exterior Access Route | M. Route not maintained in operable working condition O. Vertical clearance < 80" above ground | Walkway from Pond to Concord Road | Exterior | N/A | Priority 1 | Program Access | Ensure the accessible route is maintained in operable working condition. Trim low hanging tree branches. (Cost estimate for a 20' long 4' wide stone dust route.) | 1 | 840
9 | Heritage Park | A. Exterior Access Route | N. Accessible route not provided | Cricket Pond | Exterior | N/A | Priority 1 | Program Access | Locate sign identifying pond on an accessible route. | 1 | 0
10 | Heritage Park | A. Exterior Access Route | N. Accessible route not provided | Dogwood Path Plaque | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided to the plaque. (Cost estimate for a 6' long by 4' wide stone dust walkway.) | 1 | 192
11 | Heritage Park | A. Exterior Access Route | N. Accessible route not provided | Entrance from Dogwood Path to 9/11 Memorial | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided between the dogwood path and the 9/11 Memorial path. (Cost estimate for a 20' long by 4' wide stone dust walkway.) | 1 | 640
12 | Heritage Park | A. Exterior Access Route | N. Accessible route not provided | Near Stairs to Old Sudbury Road | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided. (Cost estimate for a 6' long by 4' wide stone dust walkway.) | 1 | 192
13 | Heritage Park | A. Exterior Access Route | N. Accessible route not provided | Plaque Along Walkway by Pond and 9/11 Memorial | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided. (Cost estimate for a 10' long by 4' wide stone dust walkway.) | 1 | 320
14 | Heritage Park | A. Exterior Access Route | N. Accessible route not provided | Walkway from Pond to Concord Road | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided to each plaque. (Cost estimate for a 6' long by 4' wide stone dust walkway.) | 2 | 384
15 | Heritage Park | G. Entrance | B. Entrance not on an accessible route | Main Entrance from Old Sudbury Road | Exterior | N/A | Priority 1 | Program Access | Provide a directional sign indicating the location of the nearest accessible entrance. | 1 | 346
16 | Heritage Park | D. Stairways | N. Handrails not provided | Main Entrance from Old Sudbury Road | Exterior | N/A | Priority 3 | Additional Access | Provide handrails. (Cost estimate for 20' of metal handrail.) | 1 | 1480
17 | Heritage Park | J. Picnic Tables | G. Toe or knee clearance at table not provided H. Picnic table not on an accessible route | Near Old Sudbury Road Entrance | Exterior | N/A | Priority 1 | Program Access | Provide at least one picnic table with top between 28"- 34" above the ground and 27" clear height underneath. Ensure that the dining surface is connected to an accessible route. (Cost for an accessible picnic table.) | 1 | 1400
18 | Heritage Park | J. Picnic Tables | G. Toe or knee clearance at table not provided H. Picnic table not on an accessible route | Walkway South of Pond | Exterior | N/A | Priority 1 | Program Access | Provide at least one picnic table with top between 28"- 34" above the ground and 27" clear height underneath. Ensure that the dining surface is connected to an accessible route. (Cost estimate for 20' long 4' wide stone dust walkway and a new accessible picnic table.) | 1 | 2040
19 | Heritage Park | L. Benches | A. No accessible route to one bench in this area | Along Walkway by Pond | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to at least one bench in this area. (Cost estimate for a 10' long by 4' wide stone dust walkway.) | 1 | 320
20 | Heritage Park | L. Benches | A. No accessible route to one bench in this area | Dogwood Path Bench After Bridge by 9/11 Memorial | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to at least one bench in this area. (Cost estimate for a 10 long by 4' wide stone dust walkway.) | 1 | 320
21 | Heritage Park | L. Benches | A. No accessible route to one bench in this area | Dogwood Path Bench Before Bridge by Concord Road | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to at least one bench in this area. (Cost estimate for a 6' long by 4' wide stone dust walkway.) | 1 | 192
22 | Heritage Park | L. Benches | A. No accessible route to one bench in this area | Walkway from 9/11 Memorial to Pond | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to at least one bench in this area. (Cost estimate for a 6' long by 4' wide stone dust walkway.) | 1 | 192
23 | Heritage Park | L. Benches | A. No accessible route to one bench in this area | Walkway from Old Sudbury Road to 9/11 Memorial | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to at least one bench in this area. (Cost estimate for a 10' long by 4' wide stone dust walkway.) | 1 | 320
24 | Heritage Park | L. Benches | A. No accessible route to one bench in this area | Walkway South of Pond | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to at least one bench in this area. (Cost estimate for a 6' long by 4' wide stone dust walkway.) | 1 | 192
25 | Heritage Park | L. Benches | A. No accessible route to one bench in this area | Walkway South of Pond | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to at least one bench in this area. (Cost estimate for 10' long 4' wide stone dust walkway.) | 1 | 320
26 | Heritage Park | N/A | N/A | 9/11 Memorial | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing space alongside one bench in each area for a wheelchair user to sit shoulder to shoulder with a person seated on the bench. | 1 | 0
27 | Heritage Park | N/A | N/A | Main Entrance from Old Sudbury Road | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing visual contrast strips at stair for safety and increased visibility. | 1 | 0
28 | Heritage Park | N/A | N/A | Main Entrance from Old Sudbury Road | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing an accessible entrance to the park at this point if possible. | 1 | 0
29 | Heritage Park | N/A | N/A | Near Pond | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a 48" wide route around all sides of one picnic table in each area. | 1 | 0
1 | Playground at 59 Horse Pond Road | A. Exterior Access Route | C. Exterior route < 48" wide G. Cross slope > 1:50 (2.00%) H. Running slope > 1:20 (5%) M. Route not maintained in operable working condition | Route from East End of Wilshire Road | Exterior | N/A | Priority 1 | Program Access | Provide an accessible route to the field from Wilshire Road. (Cost estimate for a 100' long, 4' wide accessible stone dust route.) | 1 | 3200
2 | Playground at 59 Horse Pond Road | J. Picnic Tables | G. Toe or knee clearance at table not provided H. Picnic table not on an accessible route | Sunny Picnic Area | Exterior | N/A | Priority 1 | Program Access | Provide at least one picnic table with top between 28"- 34" above the ground and 27" clear height underneath. Ensure that the picnic table is connected to an accessible route. (Cost estimate for a 130' long, 4' wide stone dust route and an accessible picnic table.) | 1 | 5560
3 | Playground at 59 Horse Pond Road | C. Field | A. Accessible spaces are not provided at team seating C. Not connected to an accessible-route | East Team Seating Area | Exterior | N/A | Priority 1 | Program Access | Provide a 36" x 48" clear floor space at team seating alongside the bench. Provide an accessible route to the team seating area. (Cost estimate for a 36" by 48" stone dust clear floor space alongside the bench and a 30' long, 4' wide accessible stone dust route from the edge of the field to the team seating area.) | 1 | 1056
4 | Playground at 59 Horse Pond Road | C. Field | A. Accessible spaces are not provided at team seating C. Not connected to an accessible-route | West Team Seating Area | Exterior | N/A | Priority 1 | Program Access | Provide a 36" x 48" clear floor space at team seating. Provide an accessible route to the team seating area. (Cost estimate for a 36" by 48" stone dust clear floor space alongside the bench and a 30' long, 4' wide accessible stone dust route from the spectator seating area to the west team seating area.) | 1 | 1152
5 | Playground at 59 Horse Pond Road | C. Field | B. Accessible spaces not provided at sidelines seating C. Not connected to an accessible-route | Spectator Seating Area | Exterior | N/A | Priority 1 | Program Access | Provide a 36" x 48" clear floor space at sidelines seating. Provide an accessible route to the the spectator seating area. (Cost estimate for a 36" by 48" stone dust clear floor space alongside the bench and an 26' long, 4' wide accessible stone dust route from the east team seating area to the spectator seating area.) | 1 | 928
6 | Playground at 59 Horse Pond Road | N/A | N/A | Sunny Picnic Area | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a 48" wide min. stable, firm and slip resistant surface under and around an accessible picnic table. | 1 | 0
1 | Ti-Sales Field | E. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces | Parking Lot | Exterior | N/A | Priority 1 | Program Access | Based on 112 estimated parking spaces, provide four (4) car accessible parking spaces and one (1) van accessible parking space. | 5 | 4000
2 | Ti-Sales Field | A. Exterior Access Route | N. Accessible route not provided | Route from Parking Lot to Field | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided. (Cost estimate for a 70' long, 4' wide stone dust route.) | 1 | 2240
1 | Willis Lake Access | A. Exterior Access Route | A. Not provided from all site arrival points | Wayside Near Picnic Area and Dock | Exterior | N/A | Priority 1 | Program Access | Ensure an accessible route is provided to the wayside.(Relocate picnic table so it does not obstruct access to the clear floor space at the wayside.) | 1 | 0
2 | Willis Lake Access | A. Exterior Access Route | H. Running slope > 1:20 (5%) | Path to Memorial | Exterior | N/A | Priority 3 | Additional Access | Reduce running slope to be no steeper than 1:20 (5%). (Reducing running slope on path to memorial may be technically infeasible.) | 1 | 0
3 | Willis Lake Access | A. Exterior Access Route | J. Level changes > 1/4" | Near Memorial and Exterior Stairs | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. (Cost based on a 4'x4' asphalt patch.) | 1 | 160
4 | Willis Lake Access | A. Exterior Access Route | J. Level changes > 1/4" | Dock | Exterior | N/A | Priority 3 | Additional Access | Alter change in level to be 1/4" high max. | 1 | 0
5 | Willis Lake Access | E. Off-Street Parking Lot or Garage | A. Total # of parking B. Total # of designated accessible parking spaces C. Total # of designated van accessible spaces G. Access aisle not provided N. Sign not provided O. Sign does not have the designation "Van Accessible" | Parking Area Near Dock | Exterior | N/A | Priority 1 | Program Access | Provide a compliant van accessible parking space with a marked access aisle 60" wide min. and no steeper than 1:48 (2.08%) in all directions. Provide a sign with the International Symbol of Accessibility (ISA) located 60” min. and 96" max. above the ground. Add the designation "Van Accessible" to the sign located at the van accessible space. | 1 | 1850
6 | Willis Lake Access | J. Picnic Tables | G. Toe or knee clearance at table not provided | Picnic Area by Dock | Exterior | N/A | Priority 1 | Program Access | Provide at least one picnic table with top between 28"- 34" above the ground and 27" clear height underneath. | 1 | 1400
7 | Willis Lake Access | Memorial | N/A | Memorial | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend, since providing an accessible route to the memorial may be technically infeasible, including some photos and descriptions of the memorial at the wayside by the beach so individuals who are unable to access the memorial can see and learn about it. | 1 | 0
8 | Willis Lake Access | Picnic Table | N/A | Picnic Area by Dock | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a 48" wide min. stable, firm and slip resistant surface such as stone dust under and around an accessible picnic table once one is placed in the picnic area by the dock. | 1 | 0
9 | Willis Lake Access | Sign | N/A | Lake Shore Drive | Exterior | N/A | Priority 4 | Enhanced Usability | Recommend providing a sign at the intersection of Lake Shore Drive and Elmwood Avenue directing visitors to Willis Lake Park. | 1 | 0